EQUIPMENT DETAILS

| Equipment Tag: | [UPS-001] | Location: | [Building / Room / Area] |  |
| --- | --- | --- | --- | --- |
| Make / Model: | [e.g. APC Symmetra / Eaton 9395] | Rated kVA: | [kVA] |  |
| Battery Type: | [VRLA / Li-Ion / NiCd] | Battery Install Date: | [MM/YYYY] |  |
| No. of Battery Strings: | [Count] | Cells per String: | [Count] |  |
| Input Voltage: | [___V 3ph+N] | Output Voltage: | [___V 3ph+N] |  |

INSPECTION CHECKLIST

| Pass [ ] | Fail [ ] | N/A [ ] | Defect [ ] | Use tick (v) in the frequency column if inspection was performed and result noted in Remarks. |
| --- | --- | --- | --- | --- |

| No. | Inspection / Maintenance Item | Std. | Pre | Daily | Mnthly | Annual | Findings / Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- |
| A. BATTERY SYSTEM |  |  |  |  |  |  |  |
| A1 | Battery float charge voltage -- within manufacturer spec (typically 2.25V/cell) | IEC 62040 | Pre-use | Daily | Monthly | Annual |  |
| A2 | Battery individual cell voltages -- no cell below -0.1V of average | IEC 60896 | Pre-use | Daily | Monthly | Annual |  |
| A3 | Battery temperature -- no cell above 35°C, thermal runaway check | IEC 60896 | Pre-use | Daily | Monthly | Annual |  |
| A4 | Battery terminals -- clean, tight, anti-corrosion coating applied | IEC 60896 | Pre-use | Daily | Monthly | Annual |  |
| A5 | Battery cabinet -- no bulging, leakage, or swelling cells | IEC 60896 | Pre-use | Daily | Monthly | Annual |  |
| A6 | Battery age -- replace every 3-5 years (VRLA) or per manufacturer | IEC 60896 | Pre-use | Daily | Monthly | Annual |  |
| A7 | Battery capacity test (annual) -- discharge test to confirm Ah rating | IEC 60896 | Pre-use | Daily | Monthly | Annual |  |
| A8 | Battery charger current -- within rated charging current | IEC 62040 | Pre-use | Daily | Monthly | Annual |  |
| B. INPUT (MAINS) SECTION |  |  |  |  |  |  |  |
| B1 | Mains input voltage L1-L2, L2-L3, L3-L1 -- within +/-10% nominal | IEC 62040 | Pre-use | Daily | Monthly | Annual |  |
| B2 | Mains input frequency -- 50 Hz +/- 1 Hz | IEC 62040 | Pre-use | Daily | Monthly | Annual |  |
| B3 | Mains input breaker / fuses -- correct rating, no signs of overheating | IEC 61439 | Pre-use | Daily | Monthly | Annual |  |
| B4 | Input bypass switch -- in correct position (AUTO / MANUAL) | IEC 62040 | Pre-use | Daily | Monthly | Annual |  |
| B5 | Rectifier / charger section -- no fault alarms, operating normally | IEC 62040 | Pre-use | Daily | Monthly | Annual |  |
| C. INVERTER & OUTPUT |  |  |  |  |  |  |  |
| C1 | UPS output voltage L1-L2, L2-L3, L3-L1 -- within +/-1% nominal | IEC 62040 | Pre-use | Daily | Monthly | Annual |  |
| C2 | Output frequency -- 50 Hz +/- 0.1 Hz | IEC 62040 | Pre-use | Daily | Monthly | Annual |  |
| C3 | Output load current -- check % load on display, flag if >80% | IEC 62040 | Pre-use | Daily | Monthly | Annual |  |
| C4 | Output waveform -- sinusoidal, THD < 5% (check on display or meter) | IEC 62040 | Pre-use | Daily | Monthly | Annual |  |
| C5 | Transfer time to battery -- automatic, within specified ms | IEC 62040 | Pre-use | Daily | Monthly | Annual |  |
| C6 | Estimated battery runtime at current load -- displayed or calculated | IEC 62040 | Pre-use | Daily | Monthly | Annual |  |
| C7 | Static bypass contactor condition -- test transfer (maintenance bypass) | IEC 62040 | Pre-use | Daily | Monthly | Annual |  |
| D. COOLING & ENVIRONMENT |  |  |  |  |  |  |  |
| D1 | Cooling fans -- all running, no unusual noise or vibration | IEC 62040 | Pre-use | Daily | Monthly | Annual |  |
| D2 | Air filters -- clean, no dust blockage on vents | IEC 62040 | Pre-use | Daily | Monthly | Annual |  |
| D3 | UPS room temperature -- below 25°C (batteries degrade above 25°C) | IEC 60896 | Pre-use | Daily | Monthly | Annual |  |
| D4 | Cable terminations -- tight, no overheating marks on insulation | IEC 60364 | Pre-use | Daily | Monthly | Annual |  |
| D5 | Control panel alarms -- all clear, no faults or warnings active | IEC 62040 | Pre-use | Daily | Monthly | Annual |  |
| D6 | Event log -- review for fault history since last inspection | IEC 62040 | Pre-use | Daily | Monthly | Annual |  |

SIGN-OFF

| Inspected By: | [Name + Position] | Company: | [Company Name] |  |
| --- | --- | --- | --- | --- |
| Signature: |  | Date: | [DD/MM/YYYY] |  |
| Next Inspection Due: | [DD/MM/YYYY] | Work Order Ref.: | [WO No. or N/A] |  |

DISCLAIMER

Generic reference checklist by FreeDocumentsHub.com. Not certified inspection advice. User assumes full responsibility for compliance with applicable local regulations and standards.

FDH-PG-03  |  FreeDocumentsHub.com  |  doers.ifti@gmail.com  |  [DELETE THIS LINE BEFORE USE]