EQUIPMENT DETAILS

| Equipment Tag: | [TX-001] | Location: | [Substation / Room] |  |
| --- | --- | --- | --- | --- |
| Make / Model: | [e.g. ABB / Siemens / Schneider] | Rating (kVA): | [kVA] |  |
| Primary Voltage: | [___kV] | Secondary Voltage: | [___V] |  |
| Type: | [ONAN / ONAF / AN / AF] | Serial No.: | [Serial No.] |  |
| Year of Manufacture: | [YYYY] | Last Oil Sample: | [DD/MM/YYYY] |  |

INSPECTION CHECKLIST

| Pass [ ] | Fail [ ] | N/A [ ] | Defect [ ] | Use tick (v) in the frequency column if inspection was performed and result noted in Remarks. |
| --- | --- | --- | --- | --- |

| No. | Inspection / Maintenance Item | Std. | Pre | Daily | Mnthly | Annual | Findings / Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- |
| A. OIL-FILLED TRANSFORMER (ONAN / OFAF) |  |  |  |  |  |  |  |
| A1 | Oil level in conservator / sight glass -- between MIN and MAX marks | IEC 60076 | Pre-use | Daily | Monthly | Annual |  |
| A2 | Oil colour -- clear to light yellow (dark = contamination / ageing) | IEC 60296 | Pre-use | Daily | Monthly | Annual |  |
| A3 | Oil temperature -- below trip setting (typically 95-110°C) | IEC 60076 | Pre-use | Daily | Monthly | Annual |  |
| A4 | Buchholz relay -- gas accumulation indicator, check for tripped contacts | IEC 60076 | Pre-use | Daily | Monthly | Annual |  |
| A5 | Pressure relief device -- not operated (check indicator) | IEC 60076 | Pre-use | Daily | Monthly | Annual |  |
| A6 | Oil leaks -- inspect all gaskets, valves, bushings, and conservator | IEC 60076 | Pre-use | Daily | Monthly | Annual |  |
| A7 | Dissolved gas analysis (DGA) sample -- annual for oil-filled units | IEC 60567 | Pre-use | Daily | Monthly | Annual |  |
| A8 | Moisture content (Tan delta) -- annual test, <20 ppm for new oil | IEC 60422 | Pre-use | Daily | Monthly | Annual |  |
| B. GENERAL (ALL TRANSFORMER TYPES) |  |  |  |  |  |  |  |
| B1 | Transformer body -- no physical damage, dents, or rust | IEC 60076 | Pre-use | Daily | Monthly | Annual |  |
| B2 | HV bushings -- clean, no cracks, no tracking marks or flashover signs | IEC 60076 | Pre-use | Daily | Monthly | Annual |  |
| B3 | LV bushings -- clean, no cracks, cable lugs tight | IEC 60076 | Pre-use | Daily | Monthly | Annual |  |
| B4 | Earthing connection -- transformer tank and neutral solidly earthed | IEC 60364 | Pre-use | Daily | Monthly | Annual |  |
| B5 | Tap changer position -- in correct position per load requirements | IEC 60214 | Pre-use | Daily | Monthly | Annual |  |
| B6 | Termination cubicle -- secure, cable glands sealed, no vermin ingress | IEC 60076 | Pre-use | Daily | Monthly | Annual |  |
| B7 | Cooling fans (OFAF) -- all running, automatic start tested | IEC 60076 | Pre-use | Daily | Monthly | Annual |  |
| B8 | Thermometer and winding temperature indicator -- calibrated | IEC 60076 | Pre-use | Daily | Monthly | Annual |  |
| C. DRY-TYPE TRANSFORMER (AN / AF) |  |  |  |  |  |  |  |
| C1 | Winding condition -- no discolouration, carbonisation, or cracking | IEC 60076-11 | Pre-use | Daily | Monthly | Annual |  |
| C2 | Enclosure -- clean, no dust accumulation on windings or core | IEC 60076-11 | Pre-use | Daily | Monthly | Annual |  |
| C3 | Forced cooling fans -- operational and starting automatically | IEC 60076-11 | Pre-use | Daily | Monthly | Annual |  |
| C4 | Moisture / condensation -- no signs on windings or connections | IEC 60076-11 | Pre-use | Daily | Monthly | Annual |  |
| C5 | Insulation resistance test (annual) -- >100 MΩ at 1kV | IEC 60076-11 | Pre-use | Daily | Monthly | Annual |  |
| D. PROTECTION & METERING |  |  |  |  |  |  |  |
| D1 | Overcurrent relays -- settings correct per protection study | IEC 60255 | Pre-use | Daily | Monthly | Annual |  |
| D2 | Differential protection relay -- test operation (annual) | IEC 60255 | Pre-use | Daily | Monthly | Annual |  |
| D3 | Energy meter -- recording, check kWh against previous period | IEC 62053 | Pre-use | Daily | Monthly | Annual |  |
| D4 | SCADA / BMS alarms -- confirm all transformer alarms mapped | IEC 61850 | Pre-use | Daily | Monthly | Annual |  |

SIGN-OFF

| Inspected By: | [Name + Position] | Company: | [Company Name] |  |
| --- | --- | --- | --- | --- |
| Signature: |  | Date: | [DD/MM/YYYY] |  |
| Next Inspection Due: | [DD/MM/YYYY] | Work Order Ref.: | [WO No. or N/A] |  |

DISCLAIMER

Generic reference checklist by FreeDocumentsHub.com. Not certified inspection advice. User assumes full responsibility for compliance with applicable local regulations and standards.

FDH-PG-04  |  FreeDocumentsHub.com  |  doers.ifti@gmail.com  |  [DELETE THIS LINE BEFORE USE]