EQUIPMENT DETAILS

| Equipment Tag: | [MCC-001] | Location: | [Building / Room / Area] |  |
| --- | --- | --- | --- | --- |
| Make / Model: | [e.g. Siemens SIVACON / Schneider Okken] | Rated Busbar Current: | [___A] |  |
| Supply Voltage: | [___V 3ph+N] | No. of Starter Bays: | [Count] |  |
| Last Thermographic Survey: | [DD/MM/YYYY] | Next Survey Due: | [DD/MM/YYYY] |  |

INSPECTION CHECKLIST

| Pass [ ] | Fail [ ] | N/A [ ] | Defect [ ] | Use tick (v) in frequency column when inspection performed; note result in Remarks. |
| --- | --- | --- | --- | --- |

| No. | Inspection / Maintenance Item | Std. | Pre | Daily | Mnthly | Annual | Findings / Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- |
| A. GENERAL INSPECTION |  |  |  |  |  |  |  |
| A1 | MCC enclosure integrity -- no dents, corrosion, IP rating maintained | IEC 61439-2 |  |  |  |  |  |
| A2 | Bus compartment -- no dust, moisture, or contamination | IEC 61439-2 |  |  |  |  |  |
| A3 | Door interlocks -- all doors have working interlocks on energised sections | IEC 61439-2 |  |  |  |  |  |
| A4 | Warning labels -- arc flash, voltage, and no-access labels in place | NFPA 70E |  |  |  |  |  |
| A5 | Earthing bus -- continuous, all sections bonded, terminations tight | IEC 60364 |  |  |  |  |  |
| A6 | Cable entries -- sealed, correctly supported, no chafing on sharp edges | IEC 61439-2 |  |  |  |  |  |
| B. INCOMER & BUSBAR |  |  |  |  |  |  |  |
| B1 | Incomer ACB / MCCB -- correct rating, CR/settings match protection study | IEC 60947 |  |  |  |  |  |
| B2 | Horizontal busbar connections -- tight, correct bolt torque per manufacturer | IEC 61439-2 |  |  |  |  |  |
| B3 | Vertical risers -- connections tight, no overheating marks | IEC 61439-2 |  |  |  |  |  |
| B4 | Busbar insulation -- no tracking, cracking, or moisture contamination | IEC 61439-2 |  |  |  |  |  |
| B5 | Thermographic survey -- IR scan of all busbars and connections (annual) | NETA MTS |  |  |  |  |  |
| B6 | Phase barriers -- all in position, no missing sections | IEC 61439-2 |  |  |  |  |  |
| C. MOTOR STARTER UNITS (FVNR / SD / VFD) |  |  |  |  |  |  |  |
| C1 | Contactor condition -- contacts not worn, pitting < 50% of contact area | IEC 60947-4 |  |  |  |  |  |
| C2 | Overload relay -- trip class setting correct for motor FLA | IEC 60947-4 |  |  |  |  |  |
| C3 | VFD (if fitted) -- no fault codes, output frequency and current within limits | IEC 61800 |  |  |  |  |  |
| C4 | Control fuses -- correct rating, not blown | IEC 60269 |  |  |  |  |  |
| C5 | Push-button and pilot lamp -- all operational | IEC 60947-5 |  |  |  |  |  |
| C6 | Motor trip history -- check event log, investigate any unexplained trips | IEC 60947-4 |  |  |  |  |  |
| C7 | Soft starter (if fitted) -- no thermal overload trips, current ramp correct | IEC 60947-4 |  |  |  |  |  |
| D. METERING & PROTECTION |  |  |  |  |  |  |  |
| D1 | Ammeter readings -- all motors within rated FLA | IEC 61439-2 |  |  |  |  |  |
| D2 | Voltmeter -- supply voltage within +/-5% nominal | IEC 60038 |  |  |  |  |  |
| D3 | Power monitoring unit -- recording and transmitting correctly | IEC 62053 |  |  |  |  |  |
| D4 | Protection relay settings -- verify annually against protection study | IEC 60255 |  |  |  |  |  |
| D5 | Earth fault relay -- test operation annually | IEC 60255 |  |  |  |  |  |

DEFECTS & CORRECTIVE ACTIONS

| No. | Item Ref. | Defect Description | Corrective Action | Target Date | Status |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  | [DD/MM/YYYY] | Open / Closed |
| 2 |  |  |  | [DD/MM/YYYY] | Open / Closed |
| 3 |  |  |  | [DD/MM/YYYY] | Open / Closed |
| 4 |  |  |  | [DD/MM/YYYY] | Open / Closed |
| 5 |  |  |  | [DD/MM/YYYY] | Open / Closed |

SIGN-OFF

| Inspected By: | [Name + Position] | Company: | [Company Name] |  |
| --- | --- | --- | --- | --- |
| Signature: |  | Date: | [DD/MM/YYYY] |  |
| Next Inspection Due: | [DD/MM/YYYY] | Work Order Ref.: | [WO No. or N/A] |  |

DISCLAIMER

Generic reference checklist by FreeDocumentsHub.com. Not certified inspection advice. User assumes full responsibility for compliance with applicable local regulations and standards.

FDH-PG-07  |  FreeDocumentsHub.com  |  doers.ifti@gmail.com  |  [DELETE THIS LINE BEFORE USE]