EQUIPMENT DETAILS

| Equipment Tag: | [ATS-001] | Location: | [Switchroom / Panel Room] |  |
| --- | --- | --- | --- | --- |
| Make / Model: | [e.g. ABB OTM / Socomec ATYS] | Rated Current: | [___A] |  |
| Normal Source: | [MDB-001 / Transformer TX-001] | Standby Source: | [Generator DG-001] |  |
| Last Full Test: | [DD/MM/YYYY] | Transfer Type: | [Open Transition / Closed Transition] |  |

INSPECTION CHECKLIST

| Pass [ ] | Fail [ ] | N/A [ ] | Defect [ ] | Use tick (v) in frequency column when inspection performed; note result in Remarks. |
| --- | --- | --- | --- | --- |

| No. | Inspection / Maintenance Item | Std. | Pre | Daily | Mnthly | Annual | Findings / Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- |
| A. PHYSICAL & MECHANICAL INSPECTION |  |  |  |  |  |  |  |
| A1 | ATS enclosure -- no damage, IP rating maintained, secured in position | IEC 60947 |  |  |  |  |  |
| A2 | Mechanical interlock -- prevents simultaneous closing of both positions | IEC 60947 |  |  |  |  |  |
| A3 | Operating mechanism -- no binding, correct travel in NORMAL / GENERATOR positions | IEC 60947 |  |  |  |  |  |
| A4 | Contacts -- check for excessive wear, pitting, or carbon build-up (annual) | IEC 60947 |  |  |  |  |  |
| A5 | Cable and busbar connections -- tight, no overheating marks | IEC 60364 |  |  |  |  |  |
| A6 | Control wiring -- no loose connections, correct labelling | IEC 60364 |  |  |  |  |  |
| B. CONTROL & TIMING FUNCTIONS |  |  |  |  |  |  |  |
| B1 | Normal source voltage sensing -- relay detects under-voltage correctly | IEC 60947 |  |  |  |  |  |
| B2 | Normal source frequency sensing -- relay detects under/over frequency | IEC 60947 |  |  |  |  |  |
| B3 | Transfer to generator: time delay -- correct delay set (typically 3-10s) | NFPA 110 |  |  |  |  |  |
| B4 | Retransfer to mains: time delay -- correct delay set (typically 5-10 min) | NFPA 110 |  |  |  |  |  |
| B5 | Generator start signal -- ATS sends correct dry contact to generator on mains failure | NFPA 110 |  |  |  |  |  |
| B6 | Open transition or closed transition -- correct mode per design | IEC 60947 |  |  |  |  |  |
| B7 | In-phase monitor (if fitted) -- prevents transfer out of phase | IEC 60947 |  |  |  |  |  |
| C. FUNCTIONAL TEST (MONTHLY) |  |  |  |  |  |  |  |
| C1 | Simulate mains failure -- drop normal supply, confirm generator starts | NFPA 110 |  |  |  |  |  |
| C2 | Transfer to generator confirmed -- ATS moves to GENERATOR position | NFPA 110 |  |  |  |  |  |
| C3 | Mains restoration -- restore normal supply, confirm retransfer after time delay | NFPA 110 |  |  |  |  |  |
| C4 | Generator cool-down and stop -- confirm generator unloads and shuts down | NFPA 110 |  |  |  |  |  |
| C5 | Transfer time recorded -- document time from mains failure to generator supply | NFPA 110 |  |  |  |  |  |
| C6 | Event log review -- check all alarm and event records | IEC 60947 |  |  |  |  |  |
| D. METERING & ALARMS |  |  |  |  |  |  |  |
| D1 | Normal source voltage -- displayed and within range | IEC 60038 |  |  |  |  |  |
| D2 | Generator source voltage -- displayed and within range when running | IEC 60038 |  |  |  |  |  |
| D3 | Load current -- within rated ATS current rating | IEC 60947 |  |  |  |  |  |
| D4 | Position indication lamps -- correct position shown on panel | IEC 60947 |  |  |  |  |  |
| D5 | Alarm outputs -- test all alarm relay outputs to SCADA / BMS | IEC 60947 |  |  |  |  |  |

DEFECTS & CORRECTIVE ACTIONS

| No. | Item Ref. | Defect Description | Corrective Action | Target Date | Status |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  | [DD/MM/YYYY] | Open / Closed |
| 2 |  |  |  | [DD/MM/YYYY] | Open / Closed |
| 3 |  |  |  | [DD/MM/YYYY] | Open / Closed |
| 4 |  |  |  | [DD/MM/YYYY] | Open / Closed |
| 5 |  |  |  | [DD/MM/YYYY] | Open / Closed |

SIGN-OFF

| Inspected By: | [Name + Position] | Company: | [Company Name] |  |
| --- | --- | --- | --- | --- |
| Signature: |  | Date: | [DD/MM/YYYY] |  |
| Next Inspection Due: | [DD/MM/YYYY] | Work Order Ref.: | [WO No. or N/A] |  |

DISCLAIMER

Generic reference checklist by FreeDocumentsHub.com. Not certified inspection advice. User assumes full responsibility for compliance with applicable local regulations and standards.

FDH-PG-08  |  FreeDocumentsHub.com  |  doers.ifti@gmail.com  |  [DELETE THIS LINE BEFORE USE]