EQUIPMENT DETAILS

| System Tag: | [BBT-001] | Location / Route: | [From: ___ To: ___] |  |
| --- | --- | --- | --- | --- |
| Make / Model: | [e.g. Siemens BD2 / Schneider Canalis] | Rated Current: | [___A] |  |
| Length of Run: | [___m] | Voltage: | [___V 3ph+N] |  |
| Last Thermographic Survey: | [DD/MM/YYYY] | Next Survey Due: | [DD/MM/YYYY] |  |

INSPECTION CHECKLIST

| Pass [ ] | Fail [ ] | N/A [ ] | Defect [ ] | Use tick (v) in frequency column when inspection performed; note result in Remarks. |
| --- | --- | --- | --- | --- |

| No. | Inspection / Maintenance Item | Std. | Pre | Daily | Mnthly | Annual | Findings / Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- |
| A. PHYSICAL INSPECTION |  |  |  |  |  |  |  |
| A1 | Housing / enclosure -- no dents, corrosion, missing covers or sections | IEC 61439-6 |  |  |  |  |  |
| A2 | Support brackets -- all in position, no missing or damaged hangers | IEC 61439-6 |  |  |  |  |  |
| A3 | Joint sections -- correctly assembled, bolts at correct torque | IEC 61439-6 |  |  |  |  |  |
| A4 | Expansion joints -- in correct position for thermal movement | IEC 61439-6 |  |  |  |  |  |
| A5 | Trunking routing -- no obstructions, access for inspection maintained | IEC 61439-6 |  |  |  |  |  |
| A6 | End caps and feed units -- secure, correctly sealed | IEC 61439-6 |  |  |  |  |  |
| B. ELECTRICAL INSPECTION |  |  |  |  |  |  |  |
| B1 | Incoming feeder connection at source end -- tight, no overheating | IEC 61439-6 |  |  |  |  |  |
| B2 | Tap-off units -- all correctly engaged, padlocked, no unauthorised taps | IEC 61439-6 |  |  |  |  |  |
| B3 | End termination box -- connections tight, cover secure | IEC 61439-6 |  |  |  |  |  |
| B4 | Earth continuity -- measure earth conductor resistance end-to-end | IEC 60364 |  |  |  |  |  |
| B5 | Insulation resistance (annual) -- >1 MΩ phase-to-earth, phase-to-phase | IEC 61439-6 |  |  |  |  |  |
| B6 | Thermographic inspection -- IR survey of all joints and tap-offs annually | NETA MTS |  |  |  |  |  |
| C. LOAD MONITORING |  |  |  |  |  |  |  |
| C1 | Load current at source end -- measure all phases, check balance | IEC 61439-6 |  |  |  |  |  |
| C2 | Voltage drop -- calculate or measure from source to end of run | IEC 60364-5-52 |  |  |  |  |  |
| C3 | Load current at each tap-off unit -- verify total does not exceed busbar rating | IEC 61439-6 |  |  |  |  |  |
| C4 | Temperature of joints under load -- spot check with IR thermometer | NETA MTS |  |  |  |  |  |

DEFECTS & CORRECTIVE ACTIONS

| No. | Item Ref. | Defect Description | Corrective Action | Target Date | Status |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  | [DD/MM/YYYY] | Open / Closed |
| 2 |  |  |  | [DD/MM/YYYY] | Open / Closed |
| 3 |  |  |  | [DD/MM/YYYY] | Open / Closed |
| 4 |  |  |  | [DD/MM/YYYY] | Open / Closed |
| 5 |  |  |  | [DD/MM/YYYY] | Open / Closed |

SIGN-OFF

| Inspected By: | [Name + Position] | Company: | [Company Name] |  |
| --- | --- | --- | --- | --- |
| Signature: |  | Date: | [DD/MM/YYYY] |  |
| Next Inspection Due: | [DD/MM/YYYY] | Work Order Ref.: | [WO No. or N/A] |  |

DISCLAIMER

Generic reference checklist by FreeDocumentsHub.com. Not certified inspection advice. User assumes full responsibility for compliance with applicable local regulations and standards.

FDH-PG-09  |  FreeDocumentsHub.com  |  doers.ifti@gmail.com  |  [DELETE THIS LINE BEFORE USE]