EQUIPMENT DETAILS

| Equipment Tag: | [PFC-001] | Location: | [MDB Room / Switchroom] |  |
| --- | --- | --- | --- | --- |
| Make / Model: | [Brand / Model] | Total kVAr Rating: | [kVAr] |  |
| No. of Steps: | [Count] | Step Size (kVAr each): | [kVAr] |  |
| Supply Voltage: | [___V 3ph] | Target Power Factor: | [0.95 / 0.97 / 0.99] |  |
| Last Power Factor Reading: | [___] | Last Thermographic Survey: | [DD/MM/YYYY] |  |

INSPECTION CHECKLIST

| Pass [ ] | Fail [ ] | N/A [ ] | Defect [ ] | Use tick (v) in frequency column when inspection performed; note result in Remarks. |
| --- | --- | --- | --- | --- |

| No. | Inspection / Maintenance Item | Std. | Pre | Daily | Mnthly | Annual | Findings / Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- |
| A. CAPACITOR UNITS |  |  |  |  |  |  |  |
| A1 | Capacitor bodies -- no bulging, leakage, cracks, or burn marks | IEC 60831 |  |  |  |  |  |
| A2 | Capacitor overpressure disconnect (OPD) -- not operated (check visual indicator) | IEC 60831 |  |  |  |  |  |
| A3 | Capacitor fuses (individual) -- correct rating, not blown | IEC 60831 |  |  |  |  |  |
| A4 | Capacitor wiring -- secure, insulation intact, no overheating | IEC 60831 |  |  |  |  |  |
| A5 | Capacitor capacitance (annual) -- measure with capacitance meter, within +/-5% rated | IEC 60831 |  |  |  |  |  |
| B. SWITCHING & CONTROL |  |  |  |  |  |  |  |
| B1 | Contactors / thyristors -- no welded contacts, correct coil voltage | IEC 60947-4 |  |  |  |  |  |
| B2 | Power factor controller -- set point correct (typically 0.95-0.99 lag) | IEC 61000-3-12 |  |  |  |  |  |
| B3 | Automatic switching -- steps adding and removing correctly with load changes | IEC 61000-3-12 |  |  |  |  |  |
| B4 | Detuning reactors (if fitted) -- no discolouration, overheating, or humming | IEC 60831 |  |  |  |  |  |
| B5 | Manual bypass / lockout switch -- functional, labelled correctly | IEC 60947 |  |  |  |  |  |
| C. HARMONIC FILTERING (if applicable) |  |  |  |  |  |  |  |
| C1 | Harmonic filter reactors -- no overheating, vibration within limits | IEC 61000 |  |  |  |  |  |
| C2 | THD (Total Harmonic Distortion) -- measure at PCC, below 5% voltage THD | IEEE 519 |  |  |  |  |  |
| C3 | Filter tuning frequency -- correct for 5th / 7th / 11th harmonic | IEC 61000 |  |  |  |  |  |
| C4 | Harmonic analyser reading -- log THD monthly | IEEE 519 |  |  |  |  |  |
| D. METERING & PERFORMANCE |  |  |  |  |  |  |  |
| D1 | Power factor reading -- at or above set point under normal load | IEC 61000-3-12 |  |  |  |  |  |
| D2 | Reactive power (kVAr) -- MVAR import from grid at or near zero | IEC 62053 |  |  |  |  |  |
| D3 | Reactive power billing -- confirm no penalty on utility bill | IEC 62053 |  |  |  |  |  |
| D4 | Enclosure temperature -- no overheating of panel or capacitors | IEC 60831 |  |  |  |  |  |
| D5 | All protective relays -- over-voltage, inrush, and earth fault operational | IEC 60255 |  |  |  |  |  |
| D6 | Thermographic survey -- IR scan of contactors and fuses (annual) | NETA MTS |  |  |  |  |  |

DEFECTS & CORRECTIVE ACTIONS

| No. | Item Ref. | Defect Description | Corrective Action | Target Date | Status |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  | [DD/MM/YYYY] | Open / Closed |
| 2 |  |  |  | [DD/MM/YYYY] | Open / Closed |
| 3 |  |  |  | [DD/MM/YYYY] | Open / Closed |
| 4 |  |  |  | [DD/MM/YYYY] | Open / Closed |
| 5 |  |  |  | [DD/MM/YYYY] | Open / Closed |

SIGN-OFF

| Inspected By: | [Name + Position] | Company: | [Company Name] |  |
| --- | --- | --- | --- | --- |
| Signature: |  | Date: | [DD/MM/YYYY] |  |
| Next Inspection Due: | [DD/MM/YYYY] | Work Order Ref.: | [WO No. or N/A] |  |

DISCLAIMER

Generic reference checklist by FreeDocumentsHub.com. Not certified inspection advice. User assumes full responsibility for compliance with applicable local regulations and standards.

FDH-PG-12  |  FreeDocumentsHub.com  |  doers.ifti@gmail.com  |  [DELETE THIS LINE BEFORE USE]