ITP IDENTIFICATION

| Project: | [Project Name] | ITP No.: | [ITP-001] |  |
| --- | --- | --- | --- | --- |
| Client: | [Client Company] | Contractor: | [Contractor Company] |  |
| System: | [Fire Detection / Integration / MEP] | Revision: | [Rev A] |  |
| Prepared By: | [QC Engineer] | Date: | [DD/MM/YYYY] |  |

INSPECTION CODES

| Code | Action | Description |
| --- | --- | --- |
| H | Hold Point | Work MUST STOP — client / third party inspection and sign-off required before proceeding |
| W | Witness Point | Client notified — work proceeds if client does not attend within agreed notice period |
| R | Review | Document / record submitted to client for review and approval — no physical attendance required |
| S | Surveillance | Random inspection — client may attend without prior notice |
| I | Information | Record submitted for information only — no approval required |

ITP SCHEDULE

| No. | Activity / Inspection Point | Acceptance Criteria | Contractor | Client | 3rd Party | Record | Reference | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| A. ENGINEERING & DESIGN |  |  |  |  |  |  |  |  |
| A1 | Design Basis Document | Approved by client | R | R | — | DBD-001 | ISO 9001 | Submit before procurement |
| A2 | Material Submittal | All items on AVL or equivalent approved | R | H | — | SUB-001 | ISO 9001 | No procurement before approval |
| A3 | FAT Procedure | Approved before FAT | R | R | — | FAT-PROC | IEC 61439 |  |
| B. FABRICATION |  |  |  |  |  |  |  |  |
| B1 | Panel enclosure inspection — IP, colour, dimensions | Match spec & drawing | I | W | — | FAT-CHK | IEC 61439 |  |
| B2 | Component installation — BOM verification | All items correct make/model/rating | I | W | — | FAT-CHK | IEC 61439 |  |
| B3 | Wiring inspection — colours, ferrules, size | Per approved schematic | I | W | — | FAT-CHK | IEC 60204 |  |
| B4 | Insulation resistance test — all circuits | >1MΩ at 500VDC | I | W | — | IR-TEST | IEC 61439 |  |
| B5 | Functional test — all interlocks | Per FAT procedure | I | H | — | FAT-REP | IEC 61439 | Client witness required |
| C. INSTALLATION |  |  |  |  |  |  |  |  |
| C1 | Panel installation — level, secure, accessible | Per drawing — IEC 61439 | I | S | — | INSTALL-CHK | IEC 61439 |  |
| C2 | Cable installation — routing, support, bending radius | Per cable schedule | I | S | — | CABLE-CHK | IEC 60228 |  |
| C3 | Termination inspection — ferrules, tightness, labels | Per termination schedule | I | W | — | TERM-CHK | IEC 60947-7 |  |
| C4 | Earth continuity — all panels and metalwork | <1Ω | I | W | — | EARTH-TEST | IEC 60364 |  |
| D. COMMISSIONING |  |  |  |  |  |  |  |  |
| D1 | Loop test — all signal loops | 0% and 100% verified | I | W | — | LOOP-TEST | ISA 5.1 |  |
| D2 | Functional test — all interlocks | Per Cause & Effect Matrix | I | H | — | SAT-REP | IEC 61511 | H — client witness mandatory |
| D3 | End-to-end system test | Full scenario test — fire + gas | I | H | — | SAT-REP | NFPA 72 | H — SAT |
| D4 | System handover | As-built dossier complete — no Cat A punches | R | H | — | HOC | ISO 9001 | H — formal handover |

SIGN-OFF

| Prepared By: | [Name + Position] | Checked By: | [Name] |  |
| --- | --- | --- | --- | --- |
| Signature: |  | Date: | [DD/MM/YYYY] |  |

DISCLAIMER

Generic reference template by FreeDocumentsHub.com. Not certified advice. User assumes full responsibility.

FDH-PM-079  |  FreeDocumentsHub.com  |  doers.ifti@gmail.com  |  [DELETE THIS LINE BEFORE USE]