## MCP & Sounder Checklist
Manual Call Points (MCP) & Sounders — Site Inspection & Commissioning Checklist
FDH-FA-MCP-01 ¦ FreeDocumentsHub.com ¦ NFPA 72 / BS 5839-1 / EN 54
Project Name: |  |  |  | Project No.:
Site / Location: |  |  |  | Client:
Contractor: |  |  |  | Inspector Name:
Date of Inspection: |  |  |  | Inspection Stage: | Pre-Comm / Commissioning / Final
A. MANUAL CALL POINTS (MCP) — VISUAL INSPECTION
No. | Inspection Item | Pass | Fail | N/A | Witness | Reference | Remarks
A1 | All MCPs are accessible and not obstructed by equipment, furniture, or storage. | ☐ | ☐ | ☐ | ☐ | NFPA 72 Cl. 17.14.3
A2 | MCP installation height is 1.4 m from finished floor level (FFL) to centre of unit. | ☐ | ☐ | ☐ | ☐ | BS 5839-1 Cl. 25.2
A3 | MCP units are free from physical damage, cracks, or broken glass elements. | ☐ | ☐ | ☐ | ☐ | EN 54-11
A4 | Red colour coding is correct and clearly visible from 3 metres distance. | ☐ | ☐ | ☐ | ☐ | NFPA 72 / BS 5839-1
A5 | MCP identification label / tag number is present and legible. | ☐ | ☐ | ☐ | ☐ | Project IFC Drawing
A6 | All cable entries are sealed and glands are tight — no exposed wiring. | ☐ | ☐ | ☐ | ☐ | IEC 60364
A7 | MCP is mounted on a solid back-box with correct fixing screws. | ☐ | ☐ | ☐ | ☐ | Manufacturer Spec
A8 | Address label (for addressable systems) matches the FACP loop programming schedule. | ☐ | ☐ | ☐ | ☐ | FACP Zone Schedule
B. MANUAL CALL POINTS (MCP) — FUNCTIONAL TEST
No. | Inspection Item | Pass | Fail | N/A | Witness | Reference | Remarks
B1 | Operate MCP by breaking glass element — confirm FACP registers correct address/zone. | ☐ | ☐ | ☐ | ☐ | NFPA 72 Cl. 14.4.4
B2 | FACP displays correct MCP zone and location description upon activation. | ☐ | ☐ | ☐ | ☐ | FACP Cause & Effect Matrix
B3 | Response time from MCP activation to FACP alarm indication is ≤ 10 seconds. | ☐ | ☐ | ☐ | ☐ | BS 5839-1 Cl. 29
B4 | All sounders and notification devices activate correctly upon MCP operation. | ☐ | ☐ | ☐ | ☐ | NFPA 72 Cl. 18.4
B5 | Any ancillary outputs (gas shut-off, HVAC shutdown, door release) respond correctly. | ☐ | ☐ | ☐ | ☐ | Cause & Effect Matrix
B6 | After test — reset MCP resettable element and confirm system returns to normal state. | ☐ | ☐ | ☐ | ☐ | Manufacturer Spec
B7 | Repeat test confirmed for all MCPs on Loop / Zone (minimum 100% tested). | ☐ | ☐ | ☐ | ☐ | NFPA 72 Cl. 14.4.4
C. SOUNDERS & BEACONS — VISUAL INSPECTION
No. | Inspection Item | Pass | Fail | N/A | Witness | Reference | Remarks
C1 | All sounders and beacons are securely fixed to walls / ceilings — no loose mounting. | ☐ | ☐ | ☐ | ☐ | EN 54-3
C2 | Sounder units are free from physical damage, discolouration, or moisture ingress. | ☐ | ☐ | ☐ | ☐ | EN 54-3
C3 | Sounder identification tag / address label matches FACP programming schedule. | ☐ | ☐ | ☐ | ☐ | FACP Zone Schedule
C4 | Cable entry glands are sealed — no exposed conductors at sounder terminal. | ☐ | ☐ | ☐ | ☐ | IEC 60364
C5 | Sounder base (if applicable) is correctly mated with detector or sounder head. | ☐ | ☐ | ☐ | ☐ | Manufacturer Spec
C6 | Beacon (strobe) units are installed at correct height — min 2.1 m from FFL. | ☐ | ☐ | ☐ | ☐ | BS 5839-1 Cl. 17
C7 | End-of-Line (EOL) device is installed at correct point in the notification circuit. | ☐ | ☐ | ☐ | ☐ | NFPA 72 Cl. 12.3
C8 | Wiring polarity at sounder terminals is correct (+ / −) per loop wiring diagram. | ☐ | ☐ | ☐ | ☐ | Loop Wiring Diagram
D. SOUNDERS & BEACONS — FUNCTIONAL TEST
No. | Inspection Item | Pass | Fail | N/A | Witness | Reference | Remarks
D1 | Activate fire alarm — all sounders in the zone operate simultaneously. | ☐ | ☐ | ☐ | ☐ | NFPA 72 Cl. 18.4
D2 | Measure sound level at furthest occupied point in zone — minimum 65 dB(A). | ☐ | ☐ | ☐ | ☐ | BS 5839-1 Cl. 17.2
D3 | Measure sound level in sleeping / rest area — minimum 75 dB(A) at pillow level. | ☐ | ☐ | ☐ | ☐ | NFPA 72 Cl. 18.4.3
D4 | Sounder tone pattern is correct (continuous / pulsing) per project specification. | ☐ | ☐ | ☐ | ☐ | Project Spec
D5 | All beacon strobes flash at correct rate (typically 1 Hz) and are visible from 10 m. | ☐ | ☐ | ☐ | ☐ | EN 54-23
D6 | Multiple strobes in the same room are synchronised — no conflicting flash patterns. | ☐ | ☐ | ☐ | ☐ | NFPA 72 Cl. 18.5.4
D7 | Sounders continue to operate on panel battery supply (mains isolated for 30 min). | ☐ | ☐ | ☐ | ☐ | NFPA 72 Cl. 10.6
D8 | Sounder circuit fault simulation (open cable) registers correctly on FACP. | ☐ | ☐ | ☐ | ☐ | BS 5839-1 Cl. 29
E. MCP & SOUNDER EQUIPMENT SCHEDULE
Tag No. | Type | Location / Description | Loop No. | Zone No. | Address | Test Result | Remarks
MCP-01 | Break-Glass MCP | Kitchen Main Exit — East Wall | L1 | Z1 | 001
MCP-02 | Break-Glass MCP | Kitchen Secondary Exit — West Wall | L1 | Z1 | 002
MCP-03 | Break-Glass MCP | Corridor — Escape Route A | L1 | Z2 | 003
SD-01 | Wall Sounder | Kitchen Area — Above MCP-01 | L2 | Z1 | 101
SD-02 | Wall Sounder | Kitchen Area — North Wall | L2 | Z1 | 102
SD-03 | Sounder / Beacon | Corridor — Escape Route A | L2 | Z2 | 103
SD-04 | Outdoor Sounder | Camp External — Main Gate | L2 | Z3 | 104
F. NON-CONFORMANCES & REMARKS
NCR No. | Item Ref. | Non-Conformance Description | Action Required | By Whom | Target Date | Close-Out Date | Status
SIGN-OFF & APPROVAL
Inspector / Technician: |  |  |  | Signature:
Client Representative: |  |  |  | Signature:
Date of Final Test: |  |  |  | Overall Result: |  | PASS / FAIL / CONDITIONAL PASS
FreeDocumentsHub.com — Professional Engineering Documents — Available 24 hours, 7 days a week — contact@freedocumentshub.com