FIRE ALARM SYSTEM

Components, Standards & Site Reference Sheet

FDH-FA-REF-01  |  Rev 01  |  May 2026  |  FreeDocumentsHub.com

| Document Code | FDH-FA-REF-01 | Applicable Standard | NFPA 72 / SAES-B-058 |
| --- | --- | --- | --- |

1. FIRE ALARM SYSTEM — OVERVIEW

A Fire Alarm System (FAS) is a life safety system designed to detect fire at the earliest possible stage, alert occupants, and trigger automatic protective actions. Every fire alarm system consists of 4 main groups of components:

| GROUP 1 | GROUP 2 | GROUP 3 | GROUP 4 |
| --- | --- | --- | --- |
| Control Equipment (FACP) | Initiating Devices (Detectors & MCP) | Notification Devices (Sounders & Beacons) | Ancillary Control (FRM, Relay Modules) |

2. FIRE ALARM CONTROL PANEL (FACP)

| Item | Description | Aramco / Site Requirement |
| --- | --- | --- |
| FACP Type | Addressable microprocessor-based fire alarm control panel | Addressable system mandatory for all Saudi Aramco facilities per SAES-B-058 |
| Approved Brands | Honeywell Notifier, Siemens Cerberus, Bosch, Hochiki | Only Aramco approved brands accepted — check approved vendor list before purchasing |
| Loop Capacity | Minimum 1 SLC loop — up to 99 to 250 addressable devices per loop | Loop capacity must support all devices with minimum 25% spare capacity |
| Power Supply | 230VAC mains + 24VDC battery backup minimum 24 hours standby | 24 hours standby + 5 minutes full alarm per NFPA 72 requirements |
| Battery Backup | Sealed VRLA maintenance-free batteries — 24VDC system | Battery must be inside climate-controlled location — not in direct sunlight |
| Display | Alphanumeric LCD display showing device address, zone, and alarm message | All alarm messages must display in English and Arabic per Aramco standard |
| Enclosure | IP30 minimum for indoor — IP55 for outdoor or dusty environments | Cabinet must be mounted at accessible height — 1.5m to centre of panel |
| Certification | UL Listed or FM Approved — IEC 62368 compliant | Only listed and certified equipment accepted on Aramco projects |

3. INITIATING DEVICES — DETECTORS

| Detector Type | Detection Method | Best Application | Spacing (NFPA 72) | NOT Suitable For |
| --- | --- | --- | --- | --- |
| Photoelectric Smoke Detector | Light scattering by smoke particles | Offices, bedrooms, corridors, storage areas | Max 93 m² coverage — 9.1m spacing | Dusty, steamy, or cooking areas |
| Ionisation Smoke Detector | Ionisation chamber disrupted by smoke | Fast-flaming fires — electrical rooms | Max 93 m² coverage | Slow smouldering fires — not preferred |
| Heat Detector — Fixed Temp | Bi-metal element — activates at set temperature | Kitchens, boiler rooms, dusty areas | Max 37 m² — 6.1m spacing | Areas requiring early warning |
| Heat Detector — Rate of Rise | Detects rapid temperature increase | Garages, attics, storage areas | Max 37 m² — 6.1m spacing | Areas with normal temp fluctuation |
| Multi-Sensor Detector | Combines smoke and heat sensors | General industrial use — best reliability | Max 93 m² coverage | Extreme temperature environments |
| Flame Detector — UV/IR | Detects UV or IR radiation from flames | Open areas, flammable liquid storage, LPG areas | Coverage per manufacturer — typically 15m range | Enclosed spaces — requires line of sight |
| Gas Detector — Catalytic | Catalytic bead sensor — combustible gas | LPG, methane, propane areas — floor level | Per manufacturer — typically 5m radius | Toxic gas detection — wrong sensor type |
| Beam Smoke Detector | Projected beam — smoke interrupts beam | Large open areas — warehouses, atriums | Up to 100m beam length — 14m spacing | Areas with physical obstructions in beam path |

4. MANUAL CALL POINTS (MCP) & INPUT MODULES

| Device | Description | Installation Requirement |
| --- | --- | --- |
| Manual Call Point (MCP) | Glass break or push-button device for manual fire alarm activation by occupant | Installed at every exit, corridor junction, and stairwell — maximum 30m travel distance to nearest MCP per NFPA 72 |
| Addressable MCP | MCP with unique address on SLC loop — identifies exact activation location on FACP | All MCPs on Aramco projects must be addressable — conventional MCPs not accepted |
| Monitor Module | Interface module connecting conventional devices to addressable SLC loop | Used to connect existing conventional detectors or pull stations to addressable system |
| Input Module | Monitors dry contact input from external systems — door contacts, flow switches | Used to interface sprinkler flow switches, tamper switches, and door hold-open devices |

5. NOTIFICATION DEVICES

| Device | Function | Sound Level | Requirement |
| --- | --- | --- | --- |
| Sounder / Horn | Audible alarm — continuous or pulsed tone warning occupants of fire alarm | Minimum 75 dB at sleeping areas — 15 dB above ambient noise level | Installed throughout building — no area more than 30m from nearest sounder |
| Sounder Beacon | Combined audible sounder and visual strobe light | 75 dB minimum + 75 cd strobe minimum | Required in noisy areas and for hearing-impaired occupants per ADA/accessibility codes |
| Visual Strobe | High-intensity xenon strobe light — visual alarm for hearing-impaired | Minimum 75 candela — synchronised strobes if multiple in same space | All strobes in same room must be synchronised to prevent seizure risk |
| Voice Evacuation | Pre-recorded or live voice messages guiding occupant evacuation | Minimum 10 dB above ambient — clear intelligibility | Mandatory in buildings above 4 floors or occupancy above 1000 persons |
| Door Holder / Release | Magnetic door holder releases fire door to close on alarm activation | Not applicable — mechanical device | Connected to FACP output module — releases on any alarm in building |

6. OUTPUT / ANCILLARY CONTROL MODULES

| Module | Function | Site Application |
| --- | --- | --- |
| FRM-1 — Relay Module | Provides dry contact output for controlling external equipment on fire alarm | Used to cut gas supply via solenoid valve and electrical supply via MCCB shunt trip on Aramco kitchen safety systems |
| Control Module | Provides supervised 24VDC output to activate notification appliances and suppression systems | Used to activate sounder circuits, suppression release, and HVAC shutdown |
| Supervisory Module | Monitors status of external equipment — valve position, pump running, tamper | Monitors sprinkler valve tamper switches and fire pump running status |
| Isolator Module | Prevents fault on one section of SLC loop from affecting rest of loop | Installed at each room or zone junction — required on Class A wiring systems |

7. ADDRESSABLE vs CONVENTIONAL — COMPARISON

| Feature | Addressable System | Conventional System |
| --- | --- | --- |
| Identification | Every device has unique address — FACP shows exact device location | Zone only — cannot identify which detector in zone activated |
| Wiring | Two-wire SLC loop — up to 250 devices on one loop | Separate wire run required per zone — more cable needed |
| Cost | Higher initial cost — lower maintenance and troubleshooting cost | Lower initial cost — higher long-term troubleshooting cost |
| Aramco Acceptance | MANDATORY for all new Aramco projects per SAES-B-058 | Not accepted on new Aramco projects — legacy systems only |
| False Alarm Handling | FACP can verify alarm before activating — reduces false alarms | Any trigger in zone activates full alarm immediately |
| Maintenance | FACP shows exact device with fault — fast troubleshooting | Must physically check every device in zone to find fault |
| Scalability | Easily expanded — add devices on existing loop | New zone requires new cable run from panel |

8. ARAMCO APPROVED BRANDS — FIRE ALARM

| Brand | Country | Products | Status |
| --- | --- | --- | --- |
| Honeywell Notifier | USA | FACP, detectors, modules, sounders — full range | Approved — widely used on Aramco projects |
| Siemens Cerberus | Germany | FACP, detectors, modules — high-end industrial | Approved — used on major Aramco facilities |
| Bosch | Germany | FACP, detectors, call points, notification | Approved — growing presence in Saudi Arabia |
| Hochiki | Japan | Detectors, call points, notification devices | Approved — competitive pricing |
| System Sensor | USA | Detectors and notification — Honeywell subsidiary | Approved — commonly used with Notifier panels |

9. SITE ENGINEER QUICK REFERENCE CHECKLIST

Before starting any fire alarm installation or commissioning — verify all items below:

|  | Check Item | Status |
| --- | --- | --- |
| ☐ | FACP brand is on Aramco approved vendor list — confirmed before purchase | Pass / Fail |
| ☐ | All detectors are addressable — no conventional devices on new installation | Pass / Fail |
| ☐ | SLC loop wiring is Class A (Style 7) — fault-tolerant ring configuration | Pass / Fail |
| ☐ | Detector spacing complies with NFPA 72 — smoke max 93m², heat max 37m² | Pass / Fail |
| ☐ | MCP installed at all exits and corridors — max 30m travel distance to nearest MCP | Pass / Fail |
| ☐ | Battery backup provides 24 hours standby plus 5 minutes full alarm | Pass / Fail |
| ☐ | All devices programmed with correct address and zone in FACP | Pass / Fail |
| ☐ | Cause and effect matrix completed and approved before commissioning | Pass / Fail |
| ☐ | All notification devices audible at minimum 75 dB throughout protected area | Pass / Fail |
| ☐ | FRM-1 modules programmed for correct output actions per cause and effect | Pass / Fail |
| ☐ | Full commissioning test completed — all devices tested and results recorded | Pass / Fail |
| ☐ | As-built drawings updated to reflect actual installation before handover | Pass / Fail |

FDH-FA-REF-01  |  Fire Alarm System Components Reference Sheet  |  Rev 01  |  May 2026

FreeDocumentsHub.com  |  contact@freedocumentshub.com  |  Available 24 Hours — 7 Days a Week