FREEDOCUMENTSHUB

ARAMCO

INSTRUMENTS & E&I QC INSPECTOR

EXAM PREPARATION GUIDE

INSTRUMENTS & E&I QC INSPECTOR EXAM PREPARATION

INSTRUMENTS & E&I QC INSPECTOR — ARAMCO APPROVAL EXAM PREPARATION GUIDE

www.freedocumentshub.com | contact@freedocumentshub.com

| Series | Saudi Aramco Instruments & E&I QC Inspector Exam Preparation |
| --- | --- |
| Document | Complete Study Guide — E&I / Instrumentation QCI Principles, Standards & 200 Questions |
| Reference Standard | IEC 61511 / IEC 60079 / SAES-J-100 / SAES-P-100 / NEC 70 / IEC 60364 |
| Level | E&I QC Inspector / Instrument Inspector / Electrical Inspector |
| Published By | FreeDocumentsHub.com |
| Year | 2026 |
| Website | www.freedocumentshub.com |

HOW TO USE THIS GUIDE

This guide is for inspectors and engineers preparing for the Saudi Aramco QC Inspector Approval exam. Study Parts 1–6, then answer all 200 questions. Check answers on the last page only.

| Section | Content |
| --- | --- |
| Part 1 — Instrument Types & Principles | Pressure, temperature, flow, level — measurement principles and inspection requirements |
| Part 2 — Electrical Installation Inspection | Cable installation, terminations, earthing, continuity — IEC 60364 and SAES-P requirements |
| Part 3 — Hazardous Area Classification | Zone classification, Ex markings, equipment selection — IEC 60079 |
| Part 4 — Functional Safety — SIL & SIS | Safety Integrity Level, SIS testing — IEC 61511 |
| Part 5 — Calibration & Loop Testing | Calibration principles, loop checks, SAT procedure |
| Part 6 — Standards, Formulas & Key Rules | IEC, SAES — E&I formulas with worked examples |
| Part 7 — 200 Exam Questions | 8 sections × 25 questions, A/B/C options, answer key last page |

Passing Score: Aim for 180+/200 (90%) before sitting the real exam.

PART 1 — INSTRUMENT TYPES & PRINCIPLES

1.1 PRESSURE INSTRUMENTS

EXAM: Instrument measurement principles appear in 20–25% of E&I QCI questions.

| Instrument | Principle | Typical Range | QCI Inspection Point |
| --- | --- | --- | --- |
| Bourdon tube gauge | Mechanical deformation of C-tube | 0–700 bar | Calibration, range, scale, isolation valve |
| DP transmitter | Two-leg differential pressure | 0–100 mbar to 700 bar | Zero/span calibration, manifold vent, drain |
| Smart pressure transmitter | Digital HART/Fieldbus | 0–700 bar | Calibration cert, configuration, loop test |
| Pressure switch | Snap action at set pressure | — | Set point verification, wiring polarity, loop test |

1.2 TEMPERATURE INSTRUMENTS

| Instrument | Type | Range | Key Inspection Check |
| --- | --- | --- | --- |
| Thermocouple | Type K (chromel-alumel) | −200 to +1260°C | Extension lead correct type — polarity — calibration |
| Thermocouple | Type J (iron-constantan) | −40 to +750°C | Not interchangeable with Type K — verify type |
| RTD Pt100 | Resistance detector | −200 to +600°C | 2/3/4-wire connection — loop resistance check |
| Bimetallic | Differential expansion | 0 to +500°C | Immersion length correct — calibration |
| Thermowell | Protection tube for TC/RTD | Per service | Material, rating, insertion length, wake frequency |

1.3 FLOW INSTRUMENTS

| Type | Principle | Straight Run | QCI Check |
| --- | --- | --- | --- |
| Orifice plate | DP across restriction | 10D up / 5D down | Bore, edge condition, orientation, DP range |
| Vortex meter | Vortex shedding frequency | 10D up / 5D down | No pipe vibration — orientation — grounding |
| Magnetic meter | Faraday's law — conductive fluid | 5D up / 3D down | Full pipe, grounding rings, zero verification |
| Coriolis meter | Mass — resonant frequency | Minimal | Self-draining orientation — vibration isolation |

PART 2 — ELECTRICAL INSTALLATION INSPECTION

2.1 CABLE INSTALLATION — QCI CHECKS

EXAM: Electrical installation inspection is 25–30% of E&I QCI exam questions.

| Check Item | Standard | Acceptance Criteria |
| --- | --- | --- |
| Cable type and size | Approved material schedule | Correct type, conductor size, insulation rating |
| Cable gland | IP and Ex rating | Correct gland for cable OD — Ex type in hazardous area |
| Bend radius | IEC 60364 | Min 6× OD multicore — 8× armoured |
| Cable segregation | SAES-P-100 | HV and LV separate trays — instruments separate from power |
| Cable tray fill | IEC 61537 | Maximum 40% fill |
| Cable labels | SAES-P-100 | Both ends — cable number matches drawing — permanent label |
| Insulation resistance | IEC 60364-6 | Min 1 MΩ @ 500VDC for LV — 1 GΩ for instrument cables |

2.2 EARTHING & BONDING

Instrument earth (clean earth) must be kept SEPARATE from power earth. Incorrect earthing causes instrument loop errors and is an NCR on Aramco projects.

| Element | Requirement | Verification Method |
| --- | --- | --- |
| Main earth electrode | < 1 Ω to true earth (IEC 62305) | Earth resistance test — Megger earth tester |
| Equipment bonding | All metallic equipment bonded to earth grid | Continuity < 1 Ω panel to earth bar |
| Instrument earth (clean) | Separate from power earth — < 1 Ω | Continuity — verify isolation from power earth |
| Cable tray bonding | Continuous earth — each section bonded | Continuity across all tray joints |
| Hazardous area bonding | Static bonding — all rotating equipment | Bond resistance < 10 Ω — label affixed |

PART 3 — HAZARDOUS AREA CLASSIFICATION

3.1 ZONE CLASSIFICATION — IEC 60079-10

EXAM: Hazardous area and Ex equipment selection appear in 20–25% of questions.

| Zone | Gas Present | Frequency | Minimum Equipment Category |
| --- | --- | --- | --- |
| Zone 0 | Continuously | Always | Cat 1G — Ex ia (intrinsic safety) only |
| Zone 1 | Likely in normal operation | Periodically | Cat 2G — Ex d, Ex e, Ex ia, Ex ib |
| Zone 2 | Unlikely — abnormal only | Occasionally | Cat 3G — Ex n (non-sparking) as minimum |
| Safe area | No hazardous atmosphere | Never | Standard equipment |

3.2 EX PROTECTION TYPES

| Ex Type | Code | Principle | Zone Suitability |
| --- | --- | --- | --- |
| Flameproof | Ex d | Contains internal explosion — strong enclosure | Zone 1 and 2 |
| Intrinsic safety | Ex ia/ib | Limits energy — incapable of ignition | Ex ia: Zone 0,1,2 ¦ Ex ib: Zone 1,2 |
| Increased safety | Ex e | No arcing parts — extra safety margins | Zone 1 and 2 |
| Purge/pressurisation | Ex p | Positive pressure — prevents gas entry | Zone 1 and 2 |
| Non-sparking | Ex n | No hot surfaces or sparks in normal operation | Zone 2 only |
| Encapsulation | Ex m | Components in compound | Zone 1 and 2 |

NEVER install standard equipment in a hazardous area. Verify Ex certificate, temperature class, gas group, and zone rating before installation.

PART 4 — FUNCTIONAL SAFETY — SIL & SIS

4.1 SAFETY INTEGRITY LEVELS

| SIL | Risk Reduction | PFD Range | Typical Aramco Application |
| --- | --- | --- | --- |
| SIL 1 | 10–100 | 0.1 to 0.01 | Low demand SIS — pump trips, local alarms |
| SIL 2 | 100–1000 | 0.01 to 0.001 | ESD systems, HIPPS — most common Aramco |
| SIL 3 | 1000–10,000 | 0.001 to 0.0001 | Fire and gas shutdown — critical ESD |
| SIL 4 | 10,000–100,000 | 0.0001 to 0.00001 | Nuclear — rarely applied oil and gas |

PFD = Probability of Failure on Demand. SIL 2 is the most common level on Aramco process safety systems.

4.2 SIS TESTING — QCI REQUIREMENTS

| Test Type | Purpose | QCI Verification |
| --- | --- | --- |
| Functional test (site) | Verify SIS actuates correctly — full trip test | Witness trip — verify all output actions occur |
| Partial stroke test | Test valve movement — SIL verification interval | Verify % stroke, speed, return to normal |
| Proof test | Full functional verification at defined interval | Witness complete trip and reset sequence |
| Response time test | Verify SIS acts within required time | Stopwatch or DCS timestamp vs SRS requirement |

PART 5 — CALIBRATION & LOOP TESTING

5.1 CALIBRATION TERMINOLOGY

EXAM: Calibration requirements and loop testing appear in every Aramco E&I QCI exam.

| Term | Definition | Acceptance Standard |
| --- | --- | --- |
| Zero | Output at minimum input (0%) | Within ±0.25% of span typical |
| Span | Full range minimum to maximum | Correct range per P&ID / data sheet |
| Accuracy | Maximum deviation from true value | Per manufacturer — typically ±0.1% |
| As-found | Reading before adjustment | Document — shows drift since last calibration |
| As-left | Reading after adjustment | Within acceptance band — signed |
| Repeatability | Same reading for same input repeatedly | Within ±0.1% of span |

5.2 LOOP TEST PROCEDURE

| Step | Activity | QCI Verification |
| --- | --- | --- |
| 1 | Verify instruments installed, calibrated, wiring checked | All certs current — continuity confirmed |
| 2 | Apply 0% (4mA) — verify 0% at DCS/control system | DCS shows 0% — no discrepancy |
| 3 | Apply 25%, 50%, 75%, 100% — record DCS at each | All readings within ±0.5% of signal |
| 4 | Verify alarm setpoints — HH, H, L, LL | Each alarm triggers at correct % — DCS log confirmed |
| 5 | Verify control actions — valve, shutdown, interlock | Correct output for each input condition |
| 6 | Record on Loop Test Record — sign and date | Witness signs — all deviations as punch items |

PART 6 — STANDARDS, FORMULAS & KEY RULES

6.1 E&I KEY FORMULAS

| Formula | Expression | Example | Application |
| --- | --- | --- | --- |
| Ohm's Law | V = I × R | 24V / 500Ω = 48mA | Loop current / voltage check |
| 4–20mA conversion | % = (mA−4)/16 × 100 | 12mA → (12-4)/16×100 = 50% | Process value from mA reading |
| Max loop resistance | R = V_supply / I_max | 24V / 0.02A = 1200Ω | 4–20mA loop design limit |
| Insulation resistance | IR = V_test / I_leakage | 500V / 500MΩ = 1μA | LV cable min 1 MΩ |

6.2 E&I STANDARDS REFERENCE

| Standard | Coverage |
| --- | --- |
| IEC 60079 series | Explosive atmospheres — zone classification, Ex equipment, installation |
| IEC 61511 | Functional safety of SIS — SIL requirements, verification |
| IEC 61508 | Functional safety — hardware and software — basis of SIL standard |
| IEC 60364 | Electrical installations — LV installation, insulation, earthing |
| SAES-J-100 | Aramco general instrumentation requirements |
| SAES-P-100 | Aramco general electrical installation requirements |
| NEC 70 / NFPA 70 | National Electrical Code — US electrical installation standard |

PART 7 — EXAM QUESTION BANK — 200 QUESTIONS

Total: 200 questions | 3 options A/B/C | Passing score 180+/200

Answer all 200 questions BEFORE checking the answer key on the last page.

| SECTION 1 (Q1–25) |  |  |  |  |
| --- | --- | --- | --- | --- |
| 1 | 4–20mA signal at 12mA represents what process value? | A 0% | B 50% — (12−4)/16 × 100 = 50% | C 75% |
| 2 | Which Ex type is suitable for Zone 0? | A Ex d (flameproof) | B Ex ia (intrinsic safety) — only type certified for Zone 0 | C Ex n (non-sparking) |
| 3 | Minimum insulation resistance LV cables per IEC 60364-6? | A 100 kΩ | B 1 MΩ at 500VDC minimum | C 10 MΩ |
| 4 | Loop test 0% signal applies what mA? | A 0 mA | B 4 mA — live zero — allows fault detection | C 20 mA |
| 5 | Loop test 100% signal applies what mA? | A 10 mA | B 20 mA — full scale signal | C 24 mA |
| 6 | Type K thermocouple range? | A 0 to 200°C | B −200 to +1260°C — chromel-alumel — most common | C 0 to 100°C |
| 7 | RTD Pt100 resistance at 0°C? | A 0 Ω | B 100 Ω — hence the Pt100 designation | C 1000 Ω |
| 8 | IEC 61511 governs? | A Electrical earthing | B Functional safety of safety instrumented systems — SIL | C Cable installation |
| 9 | SIL 2 probability of failure on demand range? | A 0.1 to 0.01 | B 0.01 to 0.001 | C 0.001 to 0.0001 |
| 10 | Instrument earth must be? | A Connected to power earth | B Separate from power earth — clean earth — prevents instrument loop noise | C Not earthed |
| 11 | Orifice plate minimum straight run upstream? | A 5D | B 10D upstream — fully developed flow profile required | C 20D |
| 12 | Magnetic flow meter requires? | A Gas flow | B Conductive fluid — Faraday's law requires conductivity | C Compressible fluid |
| 13 | Ex d marking means? | A Intrinsic safety | B Flameproof enclosure — explosion contained inside strong enclosure | C Non-sparking |
| 14 | Zone 2 minimum equipment category? | A Zone 0 equipment | B Category 3G — Ex n (non-sparking) as minimum | C Standard equipment |
| 15 | Cable tray maximum fill ratio? | A 80% | B 40% maximum fill per IEC 61537 | C 60% |
| 16 | Minimum bend radius armoured cable? | A 4× OD | B 8× OD minimum | C 2× OD |
| 17 | Shield grounding — single end. Connect at? | A Field end only | B Control room end only — floating at field end prevents ground loops | C Both ends |
| 18 | SIL 1 risk reduction factor? | A 1000 to 10,000 | B 10 to 100 | C 100 to 1000 |
| 19 | IEC 60079 series governs? | A Instrument calibration | B Explosive atmospheres — classification and Ex equipment | C Electrical installation |
| 20 | What is a Zener barrier? | A Safety relay | B Intrinsic safety device — limits voltage and current to safe levels in hazardous area | C Fuse |
| 21 | IP66 enclosure rating means? | A Waterproof only | B Dust-tight and protected against powerful water jets from all directions | C IP54 equivalent |
| 22 | HART protocol in 4–20mA loop? | A Replaces analog signal | B Superimposed digital on 4–20mA — bidirectional communication — diagnostics | C Changes signal range |
| 23 | Fail-safe valve position on instrument air failure is? | A Depends on operator | B Defined by process safety — Air-To-Open or Air-To-Close per P&ID | C Stays in position |
| 24 | Ex equipment — damaged gland found. QCI must? | A Tighten only | B NCR — replace gland — damaged Ex gland compromises zone integrity | C Accept if IP rating met |
| 25 | Loop calibration tolerance typical? | A ±5% of span | B ±0.5% of span or better — per instrument data sheet | C ±2% always |
| SECTION 2 (Q26–50) |  |  |  |  |
| 26 | As-found calibration means? | A Final calibration | B Reading before adjustment — documents drift since last calibration | C Factory calibration |
| 27 | IEC 60364-6 governs? | A Hazardous areas | B Initial verification — testing of electrical installations after installation | C Cable standards |
| 28 | Zone 1 minimum equipment category? | A Cat 1G only | B Category 2G — Ex d, Ex e, Ex ia, Ex ib all suitable | C Cat 3G |
| 29 | What is SIS? | A Safety Information System | B Safety Instrumented System — achieves or maintains safe state of process | C Sensor Interface System |
| 30 | Thermowell wake frequency calculation is? | A Optional | B Mandatory — vortex resonance with thermowell can cause fatigue failure | C Only high velocity |
| 31 | Cable segregation purpose? | A Appearance | B Prevent interference — HV/LV/instrument separate — no noise on signal cables | C Installation convenience |
| 32 | Armour bonding at cable gland purpose? | A Mechanical grip | B Continuous earth path through armour — earth fault protection | C Anti-vibration |
| 33 | Gas group IIC covers? | A Propane only | B Hydrogen and acetylene — highest energy protection required | C Methane |
| 34 | Temperature class T4 means? | A 4th generation equipment | B Maximum surface temperature 135°C — must be below gas ignition temperature | C Test class 4 |
| 35 | Continuity test of cable conductors uses? | A IR test only | B Ohmmeter or multimeter — verify each conductor connected at both ends | C Hi-pot test |
| 36 | Cable drum inspection before laying — QCI must? | A Sign delivery note only | B Verify drum ID, cable type, rating, test report — check for visible damage | C Count turns only |
| 37 | DCS 4–20mA input card — load resistor value? | A 100Ω | B 250Ω — converts 4–20mA to 1–5V at card input | C 500Ω |
| 38 | Proof test for SIL 2 SIS? | A Every 10 years | B Every 1–5 years per SIL verification — maintains PFD within SIL 2 band | C Never required |
| 39 | What is a control valve positioner? | A Valve stopper | B Device ensuring valve stem accurately follows control signal — feedback control | C Actuator type |
| 40 | Ex entity concept means? | A Standalone device | B Certified compatibility between barrier and field device — matched entity parameters | C Zener barrier only |
| 41 | Coriolis meter measures? | A Volume flow | B Mass flow directly — resonant frequency shift | C Velocity |
| 42 | Vortex meter requires what pipe condition? | A Any condition | B No excessive vibration — vibration causes false readings | C Vertical only |
| 43 | Partial stroke test on SIS valve? | A Runs full stroke | B Tests partial movement — verifies valve not seized while maintaining process flow | C Visual check only |
| 44 | QCI at loop test — DCS shows 48% at 50% input. Must? | A Accept — close enough | B NCR / punch item — deviation requires instrument re-calibration | C Average the error |
| 45 | Cable label must be at? | A Field end only | B Both ends — cable number matches drawing — permanent durable label | C Control room only |
| 46 | What is a FIM? | A Flow instrument meter | B Field termination head — housing for cable connection to instrument | C Fieldbus interface module |
| 47 | FOUNDATION Fieldbus vs 4–20mA? | A Same signal type | B Digital bus — multiple devices on single cable — diagnostic data | C Fieldbus is older technology |
| 48 | RTD 4-wire connection advantage? | A Saves cable | B Eliminates lead resistance error — highest accuracy measurement | C Lower cost |
| 49 | Hi-pot test purpose? | A Continuity check | B High potential dielectric test — verify cable insulation under elevated voltage | C Earthing test |
| 50 | In exam — stainless pipe without PMI. Answer is always? | A Accept — MTC available | B Stop — NCR — PMI mandatory for stainless and alloy — wrong grade is life-safety risk | C Do PMI at commissioning |

ANSWER KEY

STOP — Do not look until all 200 questions answered.

| Q1–20 | Ans | Q21–40 | Ans | Q41–60 | Ans | Q61–80 | Ans | Q81–100 | Ans |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | B | 21 | B | 41 | B |
| 2 | B | 22 | B | 42 | B |
| 3 | B | 23 | B | 43 | B |
| 4 | B | 24 | B | 44 | B |
| 5 | B | 25 | B | 45 | B |
| 6 | B | 26 | B | 46 | B |
| 7 | B | 27 | B | 47 | B |
| 8 | B | 28 | B | 48 | B |
| 9 | B | 29 | B | 49 | B |
| 10 | B | 30 | B | 50 | B |
| 11 | B | 31 | B |
| 12 | B | 32 | B |
| 13 | B | 33 | B |

| Your Score | Result | Action |
| --- | --- | --- |
| 180–200 | Excellent | Ready for Aramco exam. Review any weak areas. |
| 160–179 | Good | Review weak sections before sitting real exam. |
| 140–159 | Needs Work | Re-study sections below 70% before reattempting. |
| Below 140 | Not Ready | Complete full re-study of all parts. |

ABBREVIATIONS

INSTRUMENTS

| Short Form | Full Form |
| --- | --- |
| TC | Thermocouple |
| RTD | Resistance Temperature Detector |
| PT | Pressure Transmitter |
| FT | Flow Transmitter |
| LT | Level Transmitter |
| TT | Temperature Transmitter |
| DP | Differential Pressure |
| HART | Highway Addressable Remote Transducer |

ELECTRICAL

| Short Form | Full Form |
| --- | --- |
| LV | Low Voltage (up to 1000V) |
| MV | Medium Voltage (1kV–36kV) |
| IR | Insulation Resistance |
| RCD | Residual Current Device |
| MCB | Miniature Circuit Breaker |
| VSD | Variable Speed Drive |
| UPS | Uninterruptible Power Supply |

SAFETY & HAZARDOUS AREA

| Short Form | Full Form |
| --- | --- |
| SIL | Safety Integrity Level |
| SIS | Safety Instrumented System |
| ESD | Emergency Shutdown |
| PFD | Probability of Failure on Demand |
| HIPPS | High Integrity Pressure Protection System |
| ATEX | ATmosphères EXplosibles (EU Directive) |
| IECEx | IEC Scheme for Ex equipment certification |

FreeDocumentsHub.com | Free Industrial Documents & Training | Available 24/7

www.freedocumentshub.com | contact@freedocumentshub.com