## Cover Page
FreeDocumentsHub.com
Free Industrial Documents & Training — Available 24/7
FIRE ALARM SYSTEM CABLE SCHEDULE & ROUTING RECORD
Document It. Route It Right. Test It.
| Document Number | FDH-CS-FA-001
| Revision | Rev 00 — Initial Issue
| Document Type | Cable Schedule & Routing Record (Sample)
| Applicable Standard | NFPA 72 / BS 5839 / IEC 60331 / SAES-B-067
| Prepared By | FreeDocumentsHub.com
| Date of Issue | May 2026
| Status | FOR REFERENCE / ADAPTATION
© FreeDocumentsHub.com ¦ www.freedocumentshub.com ¦ SAMPLE DOCUMENT

## Cable Schedule
FIRE ALARM SYSTEM — CABLE SCHEDULE
FDH-CS-FA-001 ¦ Rev 00 ¦ NFPA 72 / BS 5839 / IEC 60331 / SAES-B-067
Project | [6 empty] | Zone / System
Prepared By | [6 empty] | Date
Approved By | [6 empty] | Revision |  |  | Rev 00
Cable Ref | Zone / Loop | From (Panel/JB) | To (Device/JB) | Cable Type & Specification | Route / Conduit Ref | Length (m) | Cores | Size mm² | IR Test (MΩ) | Continuity (Ω) | Result | Remarks
CA-001 | Zone 01 / Loop 1 | FACP — Term 1A | JB-01-A | FR-LSOH 2-Core 1.5mm² | CT-01 — Ceiling Tray | 28 | 2 | 1.5 | ∞ | >0.1 | PASS | IEC 60331-25 compliant
CA-002 | Zone 01 / Loop 1 | JB-01-A | D-A001 — Smoke Det. | FR-LSOH 2-Core 1.5mm² | CT-01 — Ceiling Tray | 12 | 2 | 1.5 | ∞ | >0.1 | PASS
CA-003 | Zone 01 / Loop 1 | JB-01-A | D-A002 — Smoke Det. | FR-LSOH 2-Core 1.5mm² | CT-01 — Ceiling Tray | 14 | 2 | 1.5 | ∞ | >0.1 | PASS
CA-004 | Zone 01 / Loop 1 | JB-01-A | D-A003 — Heat Det. | FR-LSOH 2-Core 1.5mm² | CT-01 — Ceiling Tray | 16 | 2 | 1.5 | ∞ | >0.1 | PASS
CA-005 | Zone 02 / Loop 1 | FACP — Term 2A | JB-02-A | FR-LSOH 2-Core 1.5mm² | CT-02 — Wall Conduit | 35 | 2 | 1.5 | ∞ | >0.1 | PASS
CA-006 | Zone 02 / Loop 1 | JB-02-A | D-B001 — Smoke Det. | FR-LSOH 2-Core 1.5mm² | CT-02 — Wall Conduit | 10 | 2 | 1.5 | ∞ | >0.1 | PASS
CA-007 | Zone 02 / Loop 1 | JB-02-A | MCP-01 | FR-LSOH 2-Core 1.5mm² | CT-02 — Wall Conduit | 8 | 2 | 1.5 | ∞ | >0.1 | PASS | MCP at 1.4m AFF
CA-008 | Zone 02 / Loop 1 | JB-02-A | SND-01 — Sounder | FR-LSOH 2-Core 1.5mm² | CT-02 — Wall Conduit | 11 | 2 | 1.5 | ∞ | >0.1 | PASS
CA-009 | Zone 03 / Loop 2 | FACP — Term 3A | JB-03-A | FR-LSOH 2-Core 1.5mm² | CT-03 — Ceiling Tray | 42 | 2 | 1.5 | 480 | 1.8 | FAIL | IR below threshold — investigate route
CA-010 | Zone 03 / Loop 2 | JB-03-A | D-C001 — Smoke Det. | FR-LSOH 2-Core 1.5mm² | CT-03 — Ceiling Tray | 15 | 2 | 1.5 | ∞ | >0.1 | PASS
CA-011 | Zone 03 / Loop 2 | JB-03-A | MCP-02 | FR-LSOH 2-Core 1.5mm² | CT-03 — Wall Conduit | 9 | 2 | 1.5 | ∞ | >0.1 | PASS
CA-012 | Zone 04 / Loop 2 | FACP — Term 4A | JB-04-A | MICC 2-Core 1.5mm² — High Temp | CT-04 — SS Conduit | 38 | 2 | 1.5 | ∞ | >0.1 | PASS | MICC used — high temp area
CA-013 | Zone 04 / Loop 2 | JB-04-A | D-D001 — Heat Det. | MICC 2-Core 1.5mm² — High Temp | CT-04 — SS Conduit | 14 | 2 | 1.5 | ∞ | >0.1 | PASS | Rate of rise detector
CA-014 | Zone 04 / Loop 2 | JB-04-A | D-D002 — Heat Det. | MICC 2-Core 1.5mm² — High Temp | CT-04 — SS Conduit | 16 | 2 | 1.5 | ∞ | >0.1 | PASS
CA-015 | 230VAC Supply | DB-01 — Circuit 7 | FACP — Mains Input | FR-LSOH 3-Core 2.5mm² | CT-AC — Trunking | 22 | 3 | 2.5 | ∞ | N/A | PASS | IEC 60331-1 fire resistant
CA-016 | Sounder Loop | FACP — Snd Out | SND-01 | FR-LSOH 2-Core 1.5mm² | CT-SND — Conduit | 18 | 2 | 1.5 | ∞ | >0.1 | PASS
CA-017 | Sounder Loop | SND-01 | SND-02 | FR-LSOH 2-Core 1.5mm² | CT-SND — Conduit | 12 | 2 | 1.5 | ∞ | >0.1 | PASS
CA-018 | Sounder Loop | SND-02 | SND-03 — VAD | FR-LSOH 2-Core 1.5mm² | CT-SND — Conduit | 14 | 2 | 1.5 | ∞ | >0.1 | PASS | Visual Alarm Device
SUMMARY: | [8 empty] | 18 | 17 | 1 | 0

## Cable Routing Record
FIRE ALARM SYSTEM — CABLE ROUTING RECORD
FDH-CS-FA-001 ¦ Rev 00 ¦ FreeDocumentsHub.com
A. CONDUIT & CABLE TRAY REGISTER
Route Ref | Zone Served | Route Description | Route Type | Material | Length (m) | Size (mm) | Fire Rating | Cables Carried | Remarks
CT-01 | Zone 01 | FACP to JB-01-A — Ceiling tray above server room | Cable Tray | GI Steel | 30 | 100×50 | FR — 60 min | CA-001, CA-002, CA-003, CA-004 | 300mm from power tray
CT-02 | Zone 02 | JB-02-A to devices — Wall conduit office area | Conduit | GI Steel | 38 | 25mm dia | FR — 60 min | CA-005, CA-006, CA-007, CA-008 | Surface mounted
CT-03 | Zone 03 | FACP to JB-03-A — Ceiling tray corridor | Cable Tray | GI Steel | 45 | 100×50 | FR — 60 min | CA-009, CA-010, CA-011 | IR fault on CA-009 — investigate
CT-04 | Zone 04 | FACP to JB-04-A — SS conduit kitchen | Conduit | 316 Stainless Steel | 42 | 25mm dia | FR — 90 min | CA-012, CA-013, CA-014 | MICC cable — high temp route
CT-AC | 230VAC | DB-01 to FACP mains input — trunking | Cable Trunking | PVC-Steel | 25 | 50×50 | FR — 60 min | CA-015 | Segregated from signal cables
CT-SND | Sounder | FACP sounder output to SND-01/02/03 | Conduit | GI Steel | 48 | 20mm dia | FR — 60 min | CA-016, CA-017, CA-018
B. CABLE SEPARATION COMPLIANCE CHECK — PER NFPA 72 / BS 5839
Check Ref | Route Ref | Location Description | FA Cable Ref | Power Cable Ref | Separation (mm) | Required (mm) | Compliant | Verified By | Remarks
SEP-01 | CT-01 | Server room ceiling — crossing point A | CA-001 | Power-LV-01 | 320 | 300 | ✅ YES | Site Engineer | NFPA 72 Cl.12.3.1
SEP-02 | CT-02 | Office area — wall mount section B | CA-005 to CA-008 | Power-LV-02 | 350 | 300 | ✅ YES | Site Engineer
SEP-03 | CT-03 | Corridor — ceiling crossing point C | CA-009 | Power-LV-03 | 280 | 300 | ❌ NO | Site Engineer | Non-compliant — reroute required
SEP-04 | CT-04 | Kitchen — SS conduit section | CA-012 to CA-014 | Power-LV-04 | 400 | 300 | ✅ YES | Site Engineer | MICC inherently segregated
SEP-05 | CT-AC | Mains supply trunking | CA-015 | N/A — dedicated trunking | N/A | N/A | ✅ YES | Site Engineer | Fully segregated route
C. FIRE STOPPING RECORD — WALL & FLOOR PENETRATIONS
FS Ref | Location | Drawing Ref | Cable Refs | Penetration Size | FS Material | FS Applied By | Date Applied | Inspection Result | Remarks
FS-01 | Server Room — East wall W-01 | FA-101 Rev A | CA-001 | 100×100mm | Intumescent sealant — Hilti CP 606 | Al-Shammari | 01-May-2026 | ✅ PASS
FS-02 | Office Area — North wall W-02 | FA-101 Rev A | CA-005 to CA-007 | 75×75mm | Intumescent sealant — Hilti CP 606 | Al-Shammari | 01-May-2026 | ✅ PASS
FS-03 | Corridor — Floor slab FL-01 | FA-101 Rev A | CA-009 | 50mm dia | Intumescent sealant + collar | Al-Shammari | 02-May-2026 | ✅ PASS | Collar fitted both sides
FS-04 | Kitchen — West wall W-04 | FA-101 Rev A | CA-012 to CA-014 | 100×50mm | Intumescent sealant — Hilti CP 606 | Al-Shammari | 02-May-2026 | ✅ PASS
FS-05 | Plant Room — DB wall W-05 | FA-101 Rev A | CA-015 | 50×50mm | Intumescent sealant — Hilti CP 606 | Al-Shammari | 02-May-2026 | ⚠ PENDING | Pending re-inspection after works

## IR Test & Continuity Log
FIRE ALARM CABLE — INSULATION RESISTANCE & CONTINUITY TEST LOG
FDH-CS-FA-001 ¦ Rev 00 ¦ NFPA 72 Cl.12 / BS 5839 / IEC 60364-6
ACCEPTANCE CRITERIA — PER APPLICABLE STANDARD
Parameter | [6 empty] | Acceptance Criterion
IR Test — Signal Cables (24VDC) |  |  | ≥ 1 MΩ @ 250VDC |  |  |  | IEC 60364-6 / NFPA 72 Cl.12
IR Test — Mains Supply (230VAC) |  |  | ≥ 1 MΩ @ 500VDC |  |  |  | IEC 60364-6
Continuity — Signal Cable Loop |  |  | ≤ 40 Ω/km (0.04 Ω/m max) |  |  |  | BS 5839 / NFPA 72
Continuity — Mains Supply |  |  | Per IEE Wiring Regulations |  |  |  | IEC 60364-6
INSULATION RESISTANCE & CONTINUITY TEST RESULTS
Cable Ref | Zone / Loop | Cable Type | From | To | Test Voltage | IR Result (MΩ) | Continuity (Ω) | Test Date | Test Instrument | Tested By | Result
CA-001 | Zone 01 / Loop 1 | FR-LSOH 1.5mm² 2C | FACP | JB-01-A | 250VDC | >1000 | 1.12 | 01-May-2026 | Fluke 1587 | Naushad | PASS
CA-002 | Zone 01 / Loop 1 | FR-LSOH 1.5mm² 2C | JB-01-A | D-A001 | 250VDC | >1000 | 0.85 | 01-May-2026 | Fluke 1587 | Naushad | PASS
CA-003 | Zone 01 / Loop 1 | FR-LSOH 1.5mm² 2C | JB-01-A | D-A002 | 250VDC | >1000 | 0.92 | 01-May-2026 | Fluke 1587 | Naushad | PASS
CA-004 | Zone 01 / Loop 1 | FR-LSOH 1.5mm² 2C | JB-01-A | D-A003 | 250VDC | >1000 | 1.05 | 01-May-2026 | Fluke 1587 | Naushad | PASS
CA-005 | Zone 02 / Loop 1 | FR-LSOH 1.5mm² 2C | FACP | JB-02-A | 250VDC | >1000 | 1.48 | 01-May-2026 | Fluke 1587 | Naushad | PASS
CA-006 | Zone 02 / Loop 1 | FR-LSOH 1.5mm² 2C | JB-02-A | D-B001 | 250VDC | >1000 | 0.78 | 01-May-2026 | Fluke 1587 | Naushad | PASS
CA-007 | Zone 02 / Loop 1 | FR-LSOH 1.5mm² 2C | JB-02-A | MCP-01 | 250VDC | >1000 | 0.62 | 01-May-2026 | Fluke 1587 | Naushad | PASS
CA-008 | Zone 02 / Loop 1 | FR-LSOH 1.5mm² 2C | JB-02-A | SND-01 | 250VDC | >1000 | 0.88 | 01-May-2026 | Fluke 1587 | Naushad | PASS
CA-009 | Zone 03 / Loop 2 | FR-LSOH 1.5mm² 2C | FACP | JB-03-A | 250VDC | 0.48 | 1.82 | 02-May-2026 | Fluke 1587 | Naushad | FAIL
CA-010 | Zone 03 / Loop 2 | FR-LSOH 1.5mm² 2C | JB-03-A | D-C001 | 250VDC | >1000 | 1.15 | 02-May-2026 | Fluke 1587 | Naushad | PASS
CA-011 | Zone 03 / Loop 2 | FR-LSOH 1.5mm² 2C | JB-03-A | MCP-02 | 250VDC | >1000 | 0.72 | 02-May-2026 | Fluke 1587 | Naushad | PASS
CA-012 | Zone 04 / Loop 2 | MICC 1.5mm² 2C | FACP | JB-04-A | 250VDC | >1000 | 1.62 | 02-May-2026 | Fluke 1587 | Naushad | PASS
CA-013 | Zone 04 / Loop 2 | MICC 1.5mm² 2C | JB-04-A | D-D001 | 250VDC | >1000 | 1.24 | 02-May-2026 | Fluke 1587 | Naushad | PASS
CA-014 | Zone 04 / Loop 2 | MICC 1.5mm² 2C | JB-04-A | D-D002 | 250VDC | >1000 | 1.38 | 02-May-2026 | Fluke 1587 | Naushad | PASS
CA-015 | 230VAC Supply | FR-LSOH 2.5mm² 3C | DB-01 | FACP | 500VDC | >1000 | N/A | 02-May-2026 | Fluke 1587 | Naushad | PASS
CA-016 | Sounder Loop | FR-LSOH 1.5mm² 2C | FACP | SND-01 | 250VDC | >1000 | 1.52 | 02-May-2026 | Fluke 1587 | Naushad | PASS
CA-017 | Sounder Loop | FR-LSOH 1.5mm² 2C | SND-01 | SND-02 | 250VDC | >1000 | 1.05 | 02-May-2026 | Fluke 1587 | Naushad | PASS
CA-018 | Sounder Loop | FR-LSOH 1.5mm² 2C | SND-02 | SND-03 | 250VDC | >1000 | 0.98 | 02-May-2026 | Fluke 1587 | Naushad | PASS
SUMMARY: | [8 empty] | 17 | 1 | 18

## Cable Standards Reference
FIRE ALARM CABLE — STANDARDS REFERENCE & SELECTION GUIDE
FDH-CS-FA-001 ¦ Rev 00 ¦ FreeDocumentsHub.com
A. CABLE TYPE SELECTION GUIDE — FIRE ALARM APPLICATIONS
Cable Type | Application | When to Use | Standard Reference
FR-LSOH (Fire Resistant — Low Smoke Zero Halogen) | General fire alarm signal and sounder circuits in commercial and industrial buildings | Standard choice for all signal cable runs where smoke toxicity is a concern. Mandatory in occupied buildings, public spaces, and transport facilities. Minimum 30-minute circuit integrity. | IEC 60331-25 BS 6387 Cat CWZ NFPA 72 Cl.12.2
MICC (Mineral Insulated Copper Clad) | High-temperature areas, kitchen extraction routes, boiler rooms, plant rooms, hazardous areas | Required where cable routes pass through high-temperature zones (>70°C ambient) or where extreme fire resistance is specified. 120-minute circuit integrity minimum. More expensive but provides highest fire performance. | IEC 60702-1 BS 6387 Cat CWZ SAES-B-067
FR-XLPE (Fire Resistant Cross-Linked Polyethylene) | Power supply cables and mains input to FACP where enhanced fire resistance is required | Used for 230VAC supply cables to FACP where FR-LSOH specification is required. Higher temperature rating than standard PVC. Suitable for most commercial applications. | IEC 60331-1 IEC 60332-3 NFPA 72 Cl.12
Standard PVC | NOT permitted for fire alarm system circuits | PVC cables are not fire resistant and must never be used for fire alarm signal, sounder, or power supply circuits. If found during inspection, raise an NCR immediately. | NOT COMPLIANT NFPA 72 / BS 5839 SAES-B-067
B. CABLE SIZE SELECTION — SIGNAL & POWER CIRCUITS
Circuit Type | Typical Cable Size | Max Loop Resistance | Notes
Detection Loop — Conventional | 2-Core 1.0mm² or 1.5mm² | 40 Ω per zone max | 1.5mm² preferred for longer runs and future reliability
Detection Loop — Addressable | 2-Core 1.5mm² | Manufacturer specified | Check FACP data sheet for max loop resistance and capacitance
Sounder / VAD Circuit | 2-Core 1.5mm² | Per FACP specification | Voltage drop must be calculated for long runs
FACP Mains Supply (230VAC) | 3-Core 2.5mm² | Per IEE Wiring Regs | Dedicated circuit from distribution board
Interface Module Wiring | 2-Core 1.0mm² or 1.5mm² | Per module spec | Check manufacturer data sheet
Long Cable Runs (>100m) | 2-Core 2.5mm² | Reduced resistance | Always calculate voltage drop for runs over 100m
C. MINIMUM SEPARATION FROM POWER CABLES — NFPA 72 / BS 5839
Condition | Minimum Separation | Applicable Standard | Notes
General separation — FA cable from LV power cable | 300mm (12 inches) | NFPA 72 Cl.12.3.1 BS 5839-1 Cl.26 | Applies throughout cable run
Separation at crossing points | As close as possible — perpendicular crossing only | NFPA 72 Cl.12.3.1 | Cross at 90° angle to minimise induction
Where physical separation impossible | Use metallic conduit for FA cable OR separate metallic trunking | NFPA 72 Cl.12.3.1 BS 5839-1 | Metallic shielding provides equivalent protection
Separation from HV cables (>1kV) | Consult electrical engineer — additional shielding may be required | BS 5839-1 Cl.26 | Not common in standard buildings
MICC cable — separation requirement | 50mm minimum — inherently shielded | IEC 60702-1 | MICC copper sheath provides EMI shielding
📥 Download More Free Industrial Documents
Visit FreeDocumentsHub.com — Cable Schedules, Method Statements, Commissioning Reports, NCRs, RFIs — all free
www.freedocumentshub.com — Available 24 Hours, 7 Days a Week