METHOD STATEMENT FIRE ALARM SYSTEM INSTALLATION & COMMISSIONING Industrial & Commercial Facilities

| Document No. | FDH-MS-FA-001 | Revision | Rev 00 |
| --- | --- | --- | --- |
| Prepared By | FreeDocumentsHub.com | Date | May 2026 |
| Document Type | Method Statement (Sample) | Pages | 3 |
| Applicable Standard | NFPA 72 / BS 5839 / EN 54 | Status | FOR REFERENCE ONLY |

1.  PURPOSE

This Method Statement defines the sequence of work, safety requirements, quality controls, and technical procedures for the installation and commissioning of a Conventional / Addressable Fire Alarm System (FAS) at an industrial or commercial facility. It ensures all works are executed in accordance with applicable standards and project specifications.

2.  SCOPE OF WORK

This document covers the following activities:

- Supply, installation, and termination of fire alarm system cables

- Mounting and wiring of Fire Alarm Control Panel (FACP)

- Installation of detectors: smoke, heat, and multi-sensor types

- Installation of manual call points (MCP), sounders, and strobes

- Installation of interface modules and ancillary devices

- System programming and loop configuration (addressable systems)

- Pre-commissioning checks, functional testing, and handover

3.  REFERENCE DOCUMENTS & STANDARDS

| Standard / Code | Description |
| --- | --- |
| NFPA 72 | National Fire Alarm and Signaling Code |
| BS 5839 | Fire Detection and Fire Alarm Systems for Buildings |
| EN 54 | Fire Detection and Fire Alarm Systems — European Standard |
| IEC 60331 | Fire Resistant Cables — Circuit Integrity Requirements |
| Project Specification | Client / Consultant Approved Fire Alarm System Specification |

4.  RESPONSIBILITIES

| Role | Responsibility |
| --- | --- |
| Project Manager | Overall coordination, schedule adherence, client interface |
| Site Engineer / Supervisor | Daily site supervision, quality checks, permit management |
| Fire Alarm Technician | Cable installation, device mounting, termination, testing |
| HSE Officer | Safety supervision, PTW compliance, toolbox talks |
| Commissioning Engineer | System programming, functional testing, final sign-off |

5.  MATERIALS & EQUIPMENT

All materials shall be approved by the consultant/client prior to delivery to site. The following are typically required:

- Fire Alarm Control Panel (FACP) — Conventional or Addressable as per design

- Fire Resistant Cable — 2-core or 4-core, 1.5mm² or 2.5mm² as specified

- Smoke Detectors — Photoelectric / Ionisation type

- Heat Detectors — Fixed temperature / Rate of rise type

- Manual Call Points (MCP) — Surface or flush mounted

- Sounders and Visual Alarm Devices (VAD/Strobes)

- Isolator modules, input/output modules (addressable systems)

- Cable conduit, cable trays, fixings, and junction boxes

- Commissioning tools: laptop with FACP software, multimeter, loop tester

6.  METHOD OF EXECUTION

Works shall be executed in the following sequence:

6.1  Pre-Installation Checks

- Obtain approved drawings, specifications, and Material Approval (MAS) for all equipment.

- Issue Permit to Work (PTW) and conduct toolbox talk with all personnel.

- Verify the installation area is clear and structurally ready.

- Confirm cable routes on approved drawings with site engineer.

6.2  Cable Installation

- Install cable tray or conduit along approved routes, maintaining minimum 300mm separation from power cables.

- Pull fire resistant cables through conduit or lay on cable tray — avoid sharp bends (minimum bend radius 6× cable OD).

- Label cables at both ends and at junction boxes with loop/zone number.

- Carry out insulation resistance test (IR test) — minimum 1 MΩ — before termination.

6.3  Device Installation

- Mount FACP in the designated location — typically the security room, lobby, or fire room. Secure to wall per manufacturer specs.

- Mount detector bases at ceiling level as per approved drawing. Minimum 500mm from walls, AC vents, and obstructions.

- Fit detectors to bases after all dusty works are complete. Protect during plastering and painting.

- Install MCPs at 1.4m height from finished floor level (FFL) at all exit routes.

- Install sounders and VADs at locations per drawing. Verify audibility levels meet design specification.

6.4  Termination & Wiring

- Terminate all cables at FACP, junction boxes, and field devices per approved wiring diagrams.

- Use correct ferrule numbers at each terminal. Secure with cable ties.

- No splices allowed in cable runs — all connections through approved junction boxes only.

- Seal all cable penetrations through walls and floors with approved fire stopping material.

7.  PRE-COMMISSIONING CHECKS

| No. | Check Item | Acceptance Criteria | Result |
| --- | --- | --- | --- |
| 1 | Insulation Resistance — each cable pair to earth | > 1 MΩ | Pass / Fail |
| 2 | Loop / Zone wiring continuity | < 2 Ω/zone | Pass / Fail |
| 3 | Detector smoke test — each detector | Panel alarm within 30s | Pass / Fail |
| 4 | MCP activation test — each MCP | Panel alarm, sounder activates | Pass / Fail |
| 5 | Battery backup — disconnect mains, verify alarm continues | Minimum 24 hr standby + 30 min alarm | Pass / Fail |
| 6 | Panel fault indication — open loop test | Fault LED and buzzer activate | Pass / Fail |

8.  SAFETY & HSE REQUIREMENTS

- All personnel shall hold valid safety induction and relevant trade certification.

- Permit to Work (PTW) is mandatory before commencing any installation activity.

- Personal Protective Equipment (PPE): safety helmet, safety shoes, safety glasses, gloves.

- Working at height: use approved scaffold or ladder — no standing on chairs or makeshift platforms.

- Energised panels: follow Lock Out / Tag Out (LOTO) procedure before working on live panels.

- Emergency procedure: nearest first aid kit at site office; muster point at main gate.

9.  QUALITY CONTROL & DOCUMENTATION

- All inspection activities shall be documented on the Inspection and Test Plan (ITP).

- Hold Points (HP) require consultant/client approval before proceeding.

- Witness Points (WP) require client notification — work may proceed if client does not attend.

- Red-line as-built drawings to be updated during installation and submitted at handover.

- Commissioning report, test certificates, and O&M manuals to be submitted at project close-out.

10.  ATTACHMENTS (In Full Version)

- Annex A — Risk Assessment

- Annex B — Inspection and Test Plan (ITP)

- Annex C — Cable Schedule & Termination Schedule

- Annex D — Pre-Commissioning Test Sheets

- Annex E — Commissioning Report Template

- Annex F — Zone / Loop Address Schedule

📥 Download More Free Industrial Documents Visit FreeDocumentsHub.com for free method statements, checklists, ITP templates, commissioning reports, and industrial training materials — available 24 hours, 7 days a week. www.freedocumentshub.com