## Cover Page
FreeDocumentsHub.com
Free Industrial Documents & Training — Available 24/7
FIRE ALARM SYSTEM NON-CONFORMANCE REPORT (NCR)
Identify It. Record It. Close It Properly.
| Document Number | FDH-NCR-FA-001
| Revision | Rev 00 — Initial Issue
| Document Type | Non-Conformance Report (Sample)
| Applicable Standard | NFPA 72 / BS 5839 / ISO 9001
| Prepared By | FreeDocumentsHub.com
| Date of Issue | May 2026
| Status | FOR REFERENCE / ADAPTATION
© FreeDocumentsHub.com ¦ www.freedocumentshub.com ¦ SAMPLE DOCUMENT

## NCR Register
FIRE ALARM SYSTEM — NCR REGISTER & TRACKING LOG
FDH-NCR-FA-001 ¦ Rev 00 ¦ FreeDocumentsHub.com
ALL ACTIVE AND CLOSED NON-CONFORMANCES
NCR No. | Date Raised | Zone / Area | Non-Conformance Description | Raised By | Category | Severity | Corrective Action Required | Responsible Party | Target Date | Closure Date | Status
NCR-001 | 01-May-2026 | Zone 01 — Server Room | Smoke detector D-A002 installed within 300mm of AC supply vent — violates NFPA 72 detector placement requirement | Site Engineer | Installation | MAJOR | Relocate detector minimum 500mm from vent as per approved drawing rev B | Fire Alarm Sub-Contractor | 05-May-2026 | 04-May-2026 | CLOSED
NCR-002 | 02-May-2026 | Zone 02 — Office Area | MCP-03 installed at 1.65m AFF — exceeds maximum 1.4m mounting height per BS 5839 | Consultant Inspector | Installation | MINOR | Remount MCP at 1.4m AFF — verify all MCPs on zone 02 | Fire Alarm Sub-Contractor | 06-May-2026 |  | OPEN
NCR-003 | 02-May-2026 | Cable Route — CT-03 | Cable CA-006 insulation resistance measured at 480 MΩ — below 1 MΩ minimum threshold per IEC 60331 | Commissioning Engineer | Cable / Wiring | CRITICAL | Identify and replace damaged cable section — re-test IR after replacement | Fire Alarm Sub-Contractor | 04-May-2026 |  | OPEN
NCR-004 | 03-May-2026 | FACP — Main Panel Room | Zone 04 label in FACP programmed as 'Zone 03' — incorrect zone description causes confusion during alarm | Client Representative | Commissioning | MINOR | Reprogram FACP zone labels — reconfirm all zone descriptions against approved zone schedule | Commissioning Engineer | 05-May-2026 | 03-May-2026 | CLOSED
NCR-005 | 03-May-2026 | Zone 03 — Corridor 2 | Detector B-002 non-responsive during smoke test — no alarm at panel after 60 seconds | Commissioning Engineer | Device Fault | CRITICAL | Replace detector unit — conduct root cause analysis on base wiring before replacement | Fire Alarm Sub-Contractor | 05-May-2026 |  | OPEN
NCR-006 | 04-May-2026 | Zone 01 — Server Room | Fire stopping compound missing at cable penetration through wall W-04A | HSE Officer | Installation | MAJOR | Apply approved intumescent fire stopping compound — obtain material approval before application | Fire Alarm Sub-Contractor | 06-May-2026 |  | OPEN
NCR-007 | 04-May-2026 | Sounder Circuit — All Zones | Sounder audibility at far end of Office Area B measured at 58 dB(A) — below 65 dB(A) minimum | Commissioning Engineer | Commissioning | MAJOR | Add additional sounder at Office Area B far end — re-measure audibility across all areas | Fire Alarm Sub-Contractor | 07-May-2026 |  | OPEN
NCR-008 | 05-May-2026 | Battery Backup — FACP | Battery standby test terminated at 19 hours — does not achieve 24-hour minimum requirement per NFPA 72 | Commissioning Engineer | Commissioning | CRITICAL | Replace battery with correct Ah rating per FACP manufacturer specification — retest full 24-hour standby | Fire Alarm Sub-Contractor | 08-May-2026 |  | OPEN
SUMMARY COUNT: | [5 empty] | 3 | 3 | 2 | 6 | 2 | 8

## NCR Form Template
NON-CONFORMANCE REPORT (NCR) — INDIVIDUAL FORM
FDH-NCR-FA-001 ¦ Rev 00 ¦ FreeDocumentsHub.com
A. NCR IDENTIFICATION
NCR Number |  | Date of Issue
Project Name |  | Project Number
Site / Facility |  | Zone / Area
Raised By (Name) |  | Position / Role
NCR Category | Installation / Design / Commissioning / Material | Severity | CRITICAL / MAJOR / MINOR
Reference Drawing / Doc |  | Revision
B. NON-CONFORMANCE DESCRIPTION
Describe the non-conformance in detail — what was found, where, and how it was identified:
C. APPLICABLE STANDARD / REQUIREMENT VIOLATED
Reference the specific clause, standard, drawing, or specification requirement that has been violated:
D. ROOT CAUSE ANALYSIS
Root Cause Category | Finding | Root Cause Category | Finding
Workmanship / Skill |  | Supervision Failure
Material Defect |  | Communication Breakdown
Drawing / Design Error |  | Other (specify)
E. CORRECTIVE ACTION PLAN
Action Step | Responsible Party | Target Date | Completion Date
F. VERIFICATION OF CLOSURE
Verification Item |  | Verified (Yes / No / N/A)
Corrective action physically verified on site |  | Yes / No / N/A
Re-test / re-inspection carried out and result acceptable |  | Yes / No / N/A
Photographic evidence attached |  | Yes / No / N/A
As-built drawings updated (if applicable) |  | Yes / No / N/A
NCR formally closed and recorded in NCR Register |  | Yes / No / N/A
G. AUTHORISATION & SIGNATURES
Role | Print Name | Signature | Date
NCR Raised By
Site Engineer / Supervisor
Contractor QC Manager
Client / Consultant Representative

## Categories & Severity Guide
NCR CATEGORIES, SEVERITY LEVELS & RESPONSE GUIDE
FDH-NCR-FA-001 ¦ Rev 00 ¦ FreeDocumentsHub.com
A. SEVERITY CLASSIFICATION
Severity Level | Definition | Response Time | Example
CRITICAL | Non-conformance that directly compromises life safety, system function, or regulatory compliance — system cannot be accepted until resolved | Immediate — within 24 hours | Detector non-responsive / battery backup below minimum / cable IR failure
MAJOR | Non-conformance that significantly affects installation quality or performance but does not cause immediate system failure | Within 3 working days | Incorrect detector mounting height / sounder below dB(A) minimum
MINOR | Non-conformance that is a deviation from specification but has minimal impact on system performance | Within 5 working days | Zone label error / minor cable routing deviation from drawing
B. NCR CATEGORY DEFINITIONS
Category | Description | Common Examples | Standard Reference
Installation | Physical installation deviates from approved drawings, specification, or standard | Detector position / cable route / device height / fire stopping | NFPA 72 Cl.10 / BS 5839 Pt.1 S.22
Design | Engineering design does not meet standard requirements or client specification | Detector spacing / sounder coverage / cable spec | NFPA 72 Cl.17 / BS 5839 Pt.1 S.20
Commissioning | System does not perform as required during testing and commissioning | Device non-response / battery failure / audibility / IR test | NFPA 72 Cl.14 / BS 5839 Pt.1 S.26
Material | Supplied material does not meet the approved material specification | Unapproved cable / non-EN54 compliant detector / wrong FACP model | EN 54 / Project MAS
Documentation | Project documents are incorrect, missing, or not updated to current revision | Wrong revision drawing / missing test records / unsigned ITP | ISO 9001 Cl.7.5
Workmanship | Quality of installation work is below acceptable professional standard | Poor terminations / unsupported cables / damaged device covers | Project Specification / Method Statement

## NCR Process & Closure
NCR PROCESS FLOW & CLOSURE REQUIREMENTS
FDH-NCR-FA-001 ¦ Rev 00 ¦ FreeDocumentsHub.com
| STEP 1 — Non-Conformance Identified | ⏱ Immediate
During inspection, testing, or site observation — any party can raise an NCR (site engineer, consultant, client, HSE officer, commissioning engineer)
| STEP 2 — NCR Form Raised & Numbered | ⏱ Same day
Complete the NCR Individual Form (Sheet 3). Assign unique NCR number from the register. Record date, zone, description, category, and severity level
| STEP 3 — NCR Registered in Log | ⏱ Within 24 hours
Enter the NCR in the NCR Register (Sheet 2). Status set to OPEN. Send formal notification to responsible contractor party
| STEP 4 — Root Cause Analysis | ⏱ Within 48 hours of raising
Responsible party analyses the root cause. Identify whether it is workmanship, material, design, communication, or supervision failure. Document findings
| STEP 5 — Corrective Action Plan Submitted | ⏱ Within response time per severity
Responsible party submits written Corrective Action Plan (CAP) including action steps, responsible person, and target completion date for each step
| STEP 6 — Corrective Action Implemented | ⏱ Per target date in CAP
Physical corrective work carried out on site per the approved CAP. Site engineer supervises and confirms execution
| STEP 7 — Verification & Re-Inspection | ⏱ Within 2 working days of completion
Independent verification by the raising party (consultant or site engineer). Re-test or re-inspection carried out. Results recorded. Photographic evidence taken
| STEP 8 — NCR Formally Closed | ⏱ Upon satisfactory verification
All parties sign the NCR closure section. NCR Register updated — Status changed from OPEN to CLOSED. Closure date recorded. As-built drawings updated if required
📥 Download More Free Industrial Documents
Visit FreeDocumentsHub.com — Method Statements, Commissioning Reports, NCRs, ITPs, and more — all free
www.freedocumentshub.com — Available 24 Hours, 7 Days a Week