## Cover Page
FreeDocumentsHub.com
Free Industrial Documents & Training — Available 24/7
FIRE ALARM SYSTEM REQUEST FOR INFORMATION (RFI)
Raise It Right. Track It. Get the Answer.
| Document Number | FDH-RFI-FA-001
| Revision | Rev 00 — Initial Issue
| Document Type | Request for Information Template (Sample)
| Applicable Standard | NFPA 72 / BS 5839 / EN 54 / SAES-B-067
| Prepared By | FreeDocumentsHub.com
| Date of Issue | May 2026
| Status | FOR REFERENCE / ADAPTATION
© FreeDocumentsHub.com ¦ www.freedocumentshub.com ¦ SAMPLE DOCUMENT

## RFI Register
FIRE ALARM SYSTEM — RFI REGISTER & TRACKING LOG
FDH-RFI-FA-001 ¦ Rev 00 ¦ FreeDocumentsHub.com
ALL ACTIVE AND CLOSED REQUESTS FOR INFORMATION
RFI No. | Date Raised | Subject / Question | Raised By | Directed To | Category | Urgency | Date Required | Date Answered | Days Open | Status
RFI-001 | 01-May-2026 | Smoke detector spacing — open plan kitchen area exceeds 9.3m grid — NFPA 72 Table 17.6.3.1.1 requires clarification on irregular ceiling | Al-Shammari Est. | Design Consultant | Design | HIGH | 03-May-2026 | 02-May-2026 | 1 | CLOSED
RFI-002 | 02-May-2026 | Cable specification — FR-LSOH vs MICC for cable run through kitchen hood extraction duct — which applies per SAES-B-067? | Al-Shammari Est. | Saudi Aramco Proponent | Material | HIGH | 04-May-2026 | 04-May-2026 | 2 | CLOSED
RFI-003 | 02-May-2026 | MCP mounting height conflict — architectural drawing shows MCP at 1.6m AFF but BS 5839 requires maximum 1.4m — which takes precedence? | Site Engineer — Naushad | Design Consultant | Installation | MEDIUM | 05-May-2026 |  |  | OPEN
RFI-004 | 03-May-2026 | Mitsubishi NF125-CV MCCB shunt trip coil — ST-NF 24VDC — confirm compatibility with existing MCCBs on site before procurement | Al-Shammari Est. | CAT International PM | Material | URGENT | 04-May-2026 | 03-May-2026 | 0 | CLOSED
RFI-005 | 03-May-2026 | Zone boundary — does Zone 01 (Server Room) require separate detection loop from Zone 02 (Office Area) per NFPA 72 Cl.23.4? | Commissioning Engineer | Design Consultant | Design | MEDIUM | 06-May-2026 |  |  | OPEN
RFI-006 | 04-May-2026 | Sounder audibility — BS 5839 requires 65 dB(A) at pillow level for sleeping risk areas — does kitchen area qualify? | Al-Shammari Est. | Fire Safety Consultant | Commissioning | LOW | 08-May-2026 |  |  | OPEN
RFI-007 | 04-May-2026 | Drawing revision — fire alarm layout drawing Rev A shows 14 detectors but BOQ shows 16 — which document governs procurement? | Al-Shammari Est. | Design Consultant | Documentation | HIGH | 05-May-2026 | 05-May-2026 | 1 | CLOSED
RFI-008 | 05-May-2026 | Battery backup calculation — FACP manufacturer datasheet shows 7Ah standard battery — client requires 24hr standby + 30min alarm — confirm if upgrade to 17Ah required | Commissioning Engineer | FACP Manufacturer | Commissioning | URGENT | 06-May-2026 |  |  | OPEN
SUMMARY COUNT: | [5 empty] | 2 | 3 | 2 | 4 | 4

## RFI Form Template
REQUEST FOR INFORMATION (RFI) — INDIVIDUAL FORM
FDH-RFI-FA-001 ¦ Rev 00 ¦ FreeDocumentsHub.com
A. RFI IDENTIFICATION
RFI Number |  | Date of Issue
Project Name |  | Project Number
Site / Facility |  | Zone / Area
Raised By (Name) |  | Position / Role
Directed To |  | Company / Authority
RFI Category | Design / Installation / Material / Commissioning / Documentation | Urgency | URGENT / HIGH / MEDIUM / LOW
Response Required By |  | Contract Reference
B. QUESTION / CLARIFICATION REQUIRED
State the question clearly and precisely. Reference the specific drawing, document, or clause that requires clarification:
C. REFERENCE DOCUMENTS & DRAWINGS
Document / Drawing Title |  | Revision | Clause / Sheet Ref
D. IMPACT IF NOT ANSWERED BY REQUIRED DATE
Impact Statement |  | Applicable (Yes / No)
Work stoppage — cannot proceed without clarification |  | Yes / No
Material procurement on hold — order cannot be placed |  | Yes / No
Drawing revision required — affects multiple zones |  | Yes / No
Schedule delay — critical path item |  | Yes / No
Other (specify in Section B) |  | Yes / No
E. PROPOSED SOLUTION (Optional — Contractor's Recommendation)
If the contractor has a proposed solution or preferred interpretation, state it here for the reviewer's consideration:
F. RESPONSE FROM CONSULTANT / CLIENT / AUTHORITY
Official response — to be completed by the party to whom the RFI is directed:
Response Date |  | Responded By
Response Status | Fully Answered / Partially Answered / Not Accepted | Drawing Revision Required | Yes / No
G. AUTHORISATION & SIGNATURES
Role | Print Name | Signature | Date
RFI Raised By
Contractor Project Engineer
Consultant / Client Reviewer
Saudi Aramco Representative (if applicable)

## Categories & Urgency Guide
RFI CATEGORIES, URGENCY LEVELS & RESPONSE GUIDE
FDH-RFI-FA-001 ¦ Rev 00 ¦ FreeDocumentsHub.com
A. URGENCY CLASSIFICATION & RESPONSE TIMES
Urgency | Definition | Max Response Time | Consequence If Exceeded
URGENT | RFI blocks immediate site work or procurement — work stoppage imminent | 24–48 hours | Work stops — cost and schedule impact begins immediately
HIGH | RFI affects near-term activities starting within 3–5 days — procurement or drawing issue | 3 working days | Schedule delay — procurement missed — potential rework
MEDIUM | RFI needed before next phase begins — does not stop current work | 5 working days | Phase delay if not answered before next activity
LOW | Clarification needed but does not affect current or near-term activities | 10 working days | Minor delay — can work around pending response
B. RFI CATEGORY DEFINITIONS — FIRE ALARM PROJECTS
Category | Description & When to Use | Common Fire Alarm Examples | Standard Reference
Design | Raised when the approved design drawing or specification is unclear, conflicting, or does not cover a specific site condition | Detector spacing on irregular ceiling / Zone boundary definition / Detection type selection | NFPA 72 Ch.17 / BS 5839 Pt.1 S.20
Installation | Raised when the installation method is unclear or when site conditions differ from what the drawing assumes | Cable routing conflict with structure / Panel location obstruction / Conduit type in hazardous area | NFPA 72 Ch.10 / BS 5839 Pt.1 S.22 / SAES-B-067
Material | Raised when a specified material is unavailable, requires substitution, or its specification requires clarification | Cable specification — FR-LSOH vs MICC / Detector model substitution / FACP battery Ah rating | EN 54 / IEC 60331 / Project MAS
Commissioning | Raised when a commissioning test requirement is unclear or when test results raise a question requiring engineering judgement | Audibility test method in high-noise area / Battery backup calculation / Cause & effect clarification | NFPA 72 Ch.14 / BS 5839 Pt.1 S.26
Documentation | Raised when a document conflict, missing document, or revision discrepancy requires formal clarification | Drawing revision conflict / BOQ vs drawing quantity discrepancy / ITP hold point authority | ISO 9001 Cl.7.5 / Project QMP

## RFI Process Flow
RFI PROCESS FLOW — FROM QUESTION TO ANSWER TO CLOSE
FDH-RFI-FA-001 ¦ Rev 00 ¦ FreeDocumentsHub.com
| STEP 1 — Clarification Need Identified | ⏱ Immediately on identification
During design review, material procurement, or site installation — engineer identifies a question that cannot be answered from existing approved documents without risk of error or rework
| STEP 2 — Check Existing Documents First | ⏱ Before raising — same day
Before raising an RFI, confirm the answer is not already in the approved drawings, specification, or applicable standard. Unnecessary RFIs slow projects and reduce the credibility of future RFIs
| STEP 3 — RFI Form Completed & Numbered | ⏱ Same day as identification
Complete the RFI Individual Form (Sheet 3). Assign unique RFI number from the Register. State the question precisely — reference the specific drawing, document, and clause. Assign urgency level. Identify proposed solution if available
| STEP 4 — RFI Registered & Issued | ⏱ Within 24 hours of raising
Enter the RFI in the RFI Register (Sheet 2). Status set to OPEN. Issue formally to the responsible party — consultant, client, or authority — by email with RFI form attached. The response clock starts from date of formal issue
| STEP 5 — Response Received & Reviewed | ⏱ Per urgency response time
The directing party reviews the RFI and provides a formal written response. The contractor reviews the response for completeness — if partially answered or not accepted, the RFI remains OPEN and is escalated
| STEP 6 — Work Proceeds / Drawing Updated | ⏱ Immediately after acceptance
If response is accepted — work proceeds based on the confirmed answer. If the response requires a drawing revision, the consultant issues a revised drawing referencing the RFI number. The RFI number is noted on all affected documents
| STEP 7 — RFI Formally Closed | ⏱ Upon confirmed implementation
Once the response has been received, accepted, and implemented — the RFI Register is updated: status changes from OPEN to CLOSED. Response date and days open are recorded. RFI remains in the register as a permanent project record
📥 Download More Free Industrial Documents
Visit FreeDocumentsHub.com — Method Statements, Commissioning Reports, NCRs, RFIs, ITPs — all free
www.freedocumentshub.com — Available 24 Hours, 7 Days a Week