## Cover Page
FreeDocumentsHub.com
Free Industrial Documents & Training — Available 24/7
FIRE SUPPRESSION SYSTEMS SPRINKLER · FM200 · CO2 COMPLETE SITE REFERENCE GUIDE
System Comparison · Space Selection · Inspection Schedule · Discharge Record
| Document Number | FDH-FS-001
| Revision | Rev 00 — Initial Issue
| Document Type | Fire Suppression Systems — Complete Site Reference
| Standards | NFPA 13 / NFPA 12 / NFPA 2001 / BS EN 12094 / SAES-B-067
| Systems Covered | Wet/Dry Sprinkler · FM200 (Clean Agent) · CO2
| Prepared By | FreeDocumentsHub.com
| Date | May 2026
© FreeDocumentsHub.com ¦ www.freedocumentshub.com ¦ SAMPLE DOCUMENT — FREE DOWNLOAD

## System Comparison
FIRE SUPPRESSION SYSTEMS — COMPLETE TECHNICAL COMPARISON
FDH-FS-001 ¦ Rev 00 ¦ NFPA 13 / NFPA 12 / NFPA 2001 / BS EN 12094 / SAES-B-067
Comparison Parameter | SPRINKLER SYSTEM | FM200 (CLEAN AGENT) | CO2 SYSTEM
Suppression Agent | Water — delivered through a network of pipes and sprinkler heads. Each head activates individually when heat melts the fusible link. | FM200 (Heptafluoropropane / HFC-227ea) — colourless, liquefied compressed gas stored in cylinders. Discharged as gas vapour into the protected space. | Carbon Dioxide (CO2) — stored as liquid under pressure. Discharged as gas — reduces oxygen to below the level that supports combustion.
How It Works | Heat from fire activates the sprinkler head fusible element. Water sprays over the fire area and surrounding surfaces — controls and extinguishes fire. | On detection, FM200 is discharged into the enclosed space within 10 seconds. Suppresses fire by interrupting the chemical chain reaction — not by removing oxygen. | CO2 floods the protected space and reduces oxygen concentration below 15% — insufficient to support combustion. Total flooding or local application possible.
Activation Method | Individual thermal activation — fusible link or glass bulb at each head. Only heads in the fire zone activate. Also available in deluge (all heads together). | Automatic detection (smoke/heat detector) triggers control panel. Manual abort available. Two-zone detection required for automatic release (double-knock). | Automatic detection or manual release. Two-zone detection required for automatic CO2 discharge. Pre-discharge alarm MANDATORY before release.
Protected Space Requirement | Works in open or enclosed spaces. Suitable for large warehouse areas, open plan offices, car parks. Not dependent on enclosure integrity. | Enclosed space ESSENTIAL — room must achieve and hold the required concentration (typically 8.5% vol. for 10 minutes). Gaps must be sealed. | Enclosed space ESSENTIAL — room must be sealed. CO2 concentration for total flooding: 34–75% depending on fuel. Extremely hazardous — no personnel inside.
Safety for Personnel | SAFE for personnel present at time of discharge. Water causes no toxic risk. Evacuation not required before activation. | SAFE at design concentration (max 9% vol. for occupied spaces per NFPA 2001). Above 10.5% — evacuate. Pre-discharge alarm gives evacuation time. | EXTREMELY HAZARDOUS — CO2 at fire-suppression concentrations (34%+) is immediately fatal. Space must be FULLY EVACUATED before discharge. Never use in normally occupied spaces.
Effect on Equipment & Property | WATER DAMAGE is the primary concern — all equipment and materials exposed to water spray. Not suitable for electrical switchrooms, data centres, archives, or museums. | NO damage to equipment — clean agent leaves no residue. Safe for electronics, servers, archival materials, precision instruments. Preferred for data centres. | NO residue — CO2 dissipates completely. However, thermal shock from sudden cooling can damage sensitive equipment. Pressure wave on discharge can cause structural damage.
Typical Applications | Warehouses, factories, shopping centres, office buildings, car parks, hotels, hospitals. The global standard for general building fire protection. | Data centres, server rooms, control rooms, telecommunications, museums, archival stores, laboratories, electrical switchrooms. Any area with valuable equipment. | Engine rooms, turbine halls, flammable liquid stores, paint stores, industrial process areas, power generation equipment rooms. Industrial and marine applications.
Discharge Time | Immediate — each head activates individually as it reaches activation temperature (typically 57°C–141°C depending on classification). | 10 seconds to achieve design concentration after system activation. Pre-discharge alarm typically 30 seconds before discharge. | Typically 60 seconds or less for total flooding system. Pre-discharge alarm MANDATORY — minimum 30 seconds evacuation warning before discharge.
Design Concentration | Coverage area per head: 9–21 m² (NFPA 13). Density: 4.1–12.2 mm/min depending on hazard class. K-factor specified per system design. | 8.5% vol. for Class A surface fires. 9.0% for Class B flammable liquid fires. Maximum 10.5% for normally occupied spaces per NFPA 2001 safety limit. | 34% for Class A fires. 50–75% for Class B flammable liquids. Lethal concentration to humans: above 5% (breathing), above 10% rapid incapacitation.
System Components | Sprinkler heads, pipe network, control valve, water supply (tank/pump/mains), alarm valve, flow switches, pressure gauges, inspector's test valve. | FM200 cylinders, container valve, discharge nozzles, pipe network, detection system, control panel, pre-discharge sounder, manual release station, abort switch. | CO2 cylinders (high pressure), valve manifold, discharge nozzles, pipe network, detection system, control panel, pre-discharge alarm, lockout valves, personal monitors.
Maintenance Requirements | Weekly: alarm valve check, control valve position. Monthly: flow switch test. Quarterly: water supply test. Annual: full system inspection per NFPA 25. | 6-monthly: cylinder weight check (max 5% loss), valve inspection, detection system test. Annual: full discharge simulation, nozzle inspection, room integrity test. | 6-monthly: cylinder pressure check, valve inspection. Annual: full system test, nozzle inspection, safety interlock test, CO2 monitor calibration.
Recharge After Discharge | EASY — restore water supply, replace activated sprinkler heads (individual heads only), reset alarm valve. Low cost. Fast restoration. | COSTLY — FM200 cylinders must be refilled by specialist supplier. Agent cost: approximately USD 15–25 per kg. Typical room cylinder: USD 5,000–15,000 to recharge. | MODERATE — CO2 cylinders recharged by industrial gas supplier. Cost lower than FM200. Full inspection required before recommissioning.
Environmental Impact | WATER — no environmental impact from agent itself. Large volume of water can cause flooding damage and significant drainage/disposal issues. | FM200 has a Global Warming Potential (GWP) of 3,220 — significantly higher than CO2. Not Ozone depleting. Phase-out pressure under F-Gas regulations in some regions. | CO2 is a greenhouse gas but the quantity discharged from fire suppression systems is negligible in global terms. Zero ozone depletion potential.
Governing Standard | NFPA 13 (Installation of Sprinkler Systems) BS EN 12845 (Fixed firefighting systems — Automatic sprinkler systems) SAES-B-067 (Saudi Aramco) | NFPA 2001 (Clean Agent Fire Extinguishing Systems) ISO 14520-1 (Gaseous fire-extinguishing systems) BS EN 15004 (Fixed firefighting systems — Gas extinguishing systems) | NFPA 12 (Carbon Dioxide Extinguishing Systems) ISO 6183 (Fire protection equipment — CO2 extinguishing systems) BS EN 1568 (Fire extinguishing media)
Approximate System Cost (indicative — varies by project) | USD 3–8 per sq ft installed (light hazard) USD 8–15 per sq ft (high hazard) Relatively low material cost — high labour for pipe installation | USD 25–60 per sq ft depending on room volume and agent quantity required High agent cost — cylinder infrastructure significant capital investment | USD 15–35 per sq ft for industrial applications Moderate cost — CO2 agent cheaper than FM200 but safety infrastructure cost is high
QUICK SELECTION VERDICT
USE WHEN... | General buildings, open areas, warehouses, retail, offices, car parks — any application where water damage is acceptable and personnel may be present during discharge. | Data centres, server rooms, control rooms, museums, archival stores, telecoms rooms — wherever equipment must be protected and water damage cannot be accepted. | Engine rooms, turbine rooms, flammable liquid stores, industrial process plant — unmanned areas where high-hazard fires require fast total flooding.
DO NOT USE WHEN... | Equipment damage from water is not acceptable — use FM200 or CO2 instead. | Room cannot be sealed — FM200 will not achieve required concentration. | Personnel may be present during discharge — CO2 is immediately fatal at fire suppression concentrations.

## Space Selection Guide
FIRE SUPPRESSION SYSTEM — SPACE SELECTION GUIDE
FDH-FS-001 ¦ Rev 00 ¦ NFPA 13 / NFPA 12 / NFPA 2001 / SAES-B-067
A. RECOMMENDED SYSTEM BY SPACE TYPE — 20 COMMON LOCATIONS
Space / Location | Recommended System | Alternative | Governing Standard | Key Notes & Conditions
Data Centre / Server Room | FM200 | CO2 (if unmanned) | NFPA 2001 / BS EN 15004 | Room must be sealed. Raised floor and ceiling void protection required. Room integrity test (door fan test) mandatory before commissioning.
Electrical Switchroom / MCC Room | FM200 | CO2 (if unmanned) | NFPA 2001 / IEC 60079 | Water prohibited — electrical equipment. FM200 preferred for manned access. CO2 acceptable only if lockout and signage confirmed.
Generator Room | CO2 | Sprinkler (deluge) | NFPA 12 / SAES-B-067 | High heat, flammable fuel — CO2 total flooding ideal. Pre-discharge alarm essential. Fuel isolation valve required on CO2 discharge signal.
Engine Room — Marine / Industrial | CO2 | FM200 | NFPA 12 / SOLAS | Standard marine engine room system is CO2. IMO/SOLAS requirements apply for marine. Diesel oil fire risk — CO2 preferred for speed and concentration.
Commercial Kitchen | Wet Chemical System (Kitchen Hood Suppression) | Sprinkler (supplementary) | NFPA 17A / SAES-B-067 | Grease and cooking oil fires require wet chemical agent — not water sprinkler or CO2. Separate kitchen hood suppression system mandatory. Sprinkler in adjacent areas.
Warehouse — General Storage | Sprinkler (ESFR or in-rack) | — | NFPA 13 | Hazard class determines sprinkler density. High-rack storage requires in-rack sprinklers. ESFR (Early Suppression Fast Response) heads for high storage.
Warehouse — Flammable Liquids | Deluge Sprinkler + Foam | CO2 (local application) | NFPA 11 / NFPA 16 | Foam/water deluge for flammable liquid spill fires. Containment bunding essential. Foam concentrate storage and supply system required.
Office Building — General Areas | Sprinkler | — | NFPA 13 / BS EN 12845 | Standard light hazard wet pipe sprinkler. 1 head per 21 m² maximum. Ceiling height must be considered for head spacing.
Control Room — Process Plant | FM200 | Sprinkler (pre-action) | NFPA 2001 / SAES-B-067 | Instrumentation and control equipment must be protected from water. FM200 preferred. Pre-action sprinkler acceptable if detection threshold is conservative.
Telecommunications / UPS Room | FM200 | Inert Gas (IG-55/IG-541) | NFPA 2001 | Battery room — check compatibility of suppression agent with battery off-gas (hydrogen). FM200 preferred. Ventilation interlock required.
Museum / Archive / Library | FM200 | Inert Gas | NFPA 2001 / BS EN 15004 | Water and CO2 prohibited — irreplaceable content. FM200 or inert gas only. Room integrity critical. Climate control interlock required.
Car Park — Open | Sprinkler (dry pendant) | — | NFPA 13 | Dry pendant heads used in unheated car parks to prevent pipe freezing. Drainage design critical — large water volumes from simultaneous head operation.
Car Park — Enclosed / Underground | Sprinkler + CO detection | — | NFPA 13 / BS 7346 | CO detection for vehicle exhaust required in enclosed car parks. Sprinkler for fire suppression. Smoke ventilation system linked to fire alarm.
Flammable Liquid Store — Small | CO2 (local application) | FM200 | NFPA 12 | Small enclosed flammable liquid stores. CO2 local application nozzles. Automatic door closer on CO2 discharge. Ventilation isolation required.
Paint Store / Spray Booth | Sprinkler (deluge) + Dry Powder | CO2 | NFPA 13 / NFPA 17 | Solvent-based paints — Class B fire risk. Deluge system for rapid area coverage. Dry powder portable extinguishers mandatory. Static grounding required.
Turbine Hall / Power Generation | CO2 (total flooding) | FM200 (if manned) | NFPA 12 / IEC 60079 | Large volume — CO2 preferred for cost and speed. Pre-discharge alarm 30 seconds minimum. Turbine trip interlock on CO2 discharge signal.
Hospital — Patient Areas | Sprinkler (residential heads) | — | NFPA 13 / HTM 05-02 | Residential-type sprinkler heads — lower activation temperature, wider spray. Life safety is primary objective. Concealed heads in patient rooms.
Clean Room / Pharmaceutical | FM200 | Inert Gas | NFPA 2001 / ISO 14644 | Contamination risk — no water or powder. FM200 or inert gas only. HVAC isolation on discharge to prevent agent loss. Room pressurisation considered in design.
Fuel Tank Farm / Bund Area | Foam (AFFF/FFFP) + Deluge | CO2 (local) | NFPA 11 / SAES-B-067 | Large surface area flammable liquid fires. Foam/water deluge monitors and fixed nozzles. Foam concentrate tank sizing per protected area. Bund drainage design critical.
Camp / Accommodation Block | Sprinkler (residential) | — | NFPA 13R / SAES-B-067 | Residential sprinkler system — simplified installation per NFPA 13R. Quick response heads. Domestic water supply may be sufficient for low-rise blocks.
B. QUICK DECISION GUIDE — 5 QUESTIONS TO SELECT THE RIGHT SYSTEM
Q1: Will personnel be present in the protected area during a fire event?
YES | YES → Sprinkler or FM200 only. CO2 is NOT permitted in areas with personnel present during discharge.
NO | NO → All three systems can be considered. Proceed to Q2.
Q2: Is the protected space an enclosed room that can be sealed?
YES | YES → FM200 or CO2 are viable. Proceed to Q3.
NO | NO (open area) → Sprinkler only. Gas systems require enclosure to achieve design concentration.
Q3: Is there sensitive electronic equipment, archives, or irreplaceable assets that cannot tolerate water damage?
YES | YES → FM200 or CO2 preferred. Water (sprinkler) should be avoided.
NO | NO → Sprinkler is the most cost-effective solution. Proceed to Q4 only if choosing between FM200 and CO2.
Q4: Is the fire risk primarily flammable liquid (Class B) or deep-seated ordinary combustibles (Class A)?
YES | Flammable liquid (Class B) in industrial setting → CO2 preferred for speed and cost at high concentrations.
NO | Ordinary combustibles (Class A) or mixed risk → FM200 preferred — effective at lower concentration, safer for occupied spaces.
Q5: Is the project budget the primary constraint?
YES | YES → Sprinkler is the most cost-effective. For gas systems: CO2 agent is cheaper than FM200 but safety infrastructure cost is higher.
NO | NO → FM200 is the preferred clean agent where budget allows — better safety profile, no residue, faster recharge.

## Inspection & Maintenance Log
FIRE SUPPRESSION SYSTEM — 12-MONTH INSPECTION & MAINTENANCE LOG
FDH-FS-001 ¦ Rev 00 ¦ Site: ________________ ¦ System Type: ________________ ¦ Year: ______
Project / Facility
[8 empty] | System Type | Sprinkler / FM200 / CO2
System ID / Tag
Contractor
Inspector Name
Next Major Service Due
A. WEEKLY INSPECTION CHECKLIST (All System Types)
Inspection Item | Wk 1 | Wk 2 | Wk 3 | Wk 4 | Wk 5 | Wk 6 | Wk 7 | Wk 8 | Wk 9 | Wk 10 | Wk 11 | Wk 12 | Wk 13 | Wk 14
Control valve — confirm OPEN position and tamper-proof seal intact
System pressure gauge — reading within normal operating range
Water supply / cylinder pressure — confirm adequate supply
Panel status — confirm NORMAL (no faults or alarms active)
Signage — discharge warnings and safety signs in place and legible
Access to protected area — no obstructions to sprinkler heads / nozzles
Physical damage — no visible damage to pipes, heads, cylinders, or brackets
B. MONTHLY INSPECTION CHECKLIST
Inspection Item | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | N/A | Sign-off
[ALL SYSTEMS] Flow switch and tamper switch — function test | bar: Wk 1 to Wk 12
[ALL SYSTEMS] Alarm devices — sounders and visual indicators test
[ALL SYSTEMS] Detection system — smoke/heat detector test (sample) | bar: Wk 1 to Wk 12
[ALL SYSTEMS] Emergency lighting in protected area — check operational
[SPRINKLER] Inspector's test valve — flow test and alarm activation | bar: Wk 1 to Wk 12
[SPRINKLER] Water storage tank level and pump status check
[FM200 / CO2] Cylinder weight / pressure check — record readings | bar: Wk 1 to Wk 12
[FM200 / CO2] Discharge nozzles — visual check for obstruction or damage
[FM200 / CO2] Manual release station — check accessible and clearly labelled | bar: Wk 1 to Wk 12
[FM200 / CO2] Abort switch — test function (if fitted)
[CO2 ONLY] CO2 concentration monitor / personal alarm — test calibration | bar: Wk 1 to Wk 12
[CO2 ONLY] Pre-discharge alarm — test sequence and timing (30s minimum)
C. ANNUAL INSPECTION & SERVICE CHECKLIST
Annual Inspection Item | System | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Standard | Status | Remarks
Full system flow test — confirm all heads/nozzles operate as designed | Wk 1: ALL; Wk 12: NFPA 13/12/2001; Wk 13: PENDING
Hydraulic calculation verification — confirm system still meets design | Wk 1: ALL; Wk 12: NFPA 13; Wk 13: PENDING
Pipe condition inspection — corrosion, joints, hangers, seismic bracing | Wk 1: ALL; Wk 12: NFPA 25; Wk 13: PENDING
All sprinkler heads — inspect for paint, corrosion, or physical damage | Wk 1: SPR; Wk 12: NFPA 25; Wk 13: PENDING
Replacement of any heads at or beyond 50-year service life | Wk 1: SPR; Wk 12: NFPA 25; Wk 13: PENDING
Backflow preventer — full test and certification | Wk 1: SPR; Wk 12: NFPA 25; Wk 13: PENDING
Fire pump — annual acceptance test at rated flow and pressure | Wk 1: SPR; Wk 12: NFPA 20; Wk 13: PENDING
FM200 cylinder reweigh — record weight, compare to nameplate | Wk 1: FM200; Wk 12: NFPA 2001; Wk 13: PENDING
Room door fan integrity test — confirm enclosure meets 10-minute hold | Wk 1: FM200; Wk 12: NFPA 2001; Wk 13: PENDING
Discharge simulation — confirm panel sequence and timing | Wk 1: FM200/CO2; Wk 12: NFPA 2001/12; Wk 13: PENDING
CO2 cylinder pressure and weight verification | Wk 1: CO2; Wk 12: NFPA 12; Wk 13: PENDING
CO2 safety interlock test — ventilation, door release, lockout | Wk 1: CO2; Wk 12: NFPA 12; Wk 13: PENDING
Pre-discharge alarm timing test — confirm 30s minimum warning | Wk 1: CO2; Wk 12: NFPA 12; Wk 13: PENDING
Full cause and effect matrix verification | Wk 1: ALL; Wk 12: SAES-B-067; Wk 13: PENDING
As-built drawings review and update if changes made | Wk 1: ALL; Wk 12: ISO 9001; Wk 13: PENDING

## Incident & Discharge Record
FIRE SUPPRESSION SYSTEM — INCIDENT & DISCHARGE RECORD
FDH-FS-001 ¦ Rev 00 ¦ Retain for minimum 5 years ¦ Required for Aramco / ISO 9001 audit
Facility / Site Name |  |  | System Location / Area
Responsible Safety Officer |  |  | Contact Number
Document Controller |  |  | Date of First Entry
A. SYSTEM ACTIVATION & DISCHARGE LOG
Record No. | Date of Activation | Time | Location / Zone | System Type | Activation Cause | Activation Mode | Agent Discharged | Fire Confirmed? | Damage Assessment | Recharge Status | Incident Ref No. | Investigated By / Date
001 | 12 Jan 2026 | 14:35 | Server Room — Level 2 | FM200 | Smoke detector activation — overheating UPS unit | Automatic | Yes — 28kg cylinder discharged | Yes — contained | UPS unit damaged. No structural damage. No water damage. | RECHARGED — 28 Feb 2026 | INC-2026-001 | J. Smith / 15 Jan 2026
002 | 28 Feb 2026 | 09:12 | Kitchen Hood — Canteen | Wet Chemical | Grease fire — cooking oil overheated in deep fryer | Automatic | Yes — wet chemical discharged | Yes — extinguished | Deep fryer damaged. Hood and duct — minor damage. Cleaned and recommissioned. | RECHARGED — 05 Mar 2026 | INC-2026-002 | M. Hassan / 01 Mar 2026
003 | 15 Mar 2026 | — | Warehouse Zone C | Sprinkler | FALSE ALARM — steam from cleaning equipment triggered head | Automatic (single head) | Yes — water discharged (single head, approx 80L) | No — false alarm | Wet floor — no structural damage. 1 sprinkler head replaced. | RESTORED — 15 Mar 2026 | INC-2026-003 | Safety Officer / 15 Mar 2026
004
005
006
007
008
009
010
011
012
013
014
015
B. CORRECTIVE ACTIONS & FOLLOW-UP
CA Ref | Linked Incident | Date Raised | Corrective Action Description | Assigned To | Priority | Target Date | Completion Date | Verified By | Status | Root Cause Category | Recurrence Prevention | Management Sign-off
CA-001 | INC-2026-001 | 15 Jan 2026 | Replace UPS unit with ventilated model. Install additional cooling in server room. | IT Manager | HIGH | 28 Feb 2026 | 22 Feb 2026 | Safety Officer | CLOSED | Equipment failure — inadequate ventilation | Ventilation upgrade completed. Monthly temperature monitoring added to PM schedule. | Approved — 22 Feb 2026
CA-002 | INC-2026-002 | 01 Mar 2026 | Implement monthly deep fryer inspection and cleaning procedure. Retrain kitchen staff. | Facilities Manager | MEDIUM | 31 Mar 2026 | 28 Mar 2026 | Safety Officer | CLOSED | Procedure non-compliance — maintenance gap | New procedure FMS-KIT-001 issued. All kitchen staff trained and signed off. | Approved — 28 Mar 2026
CA-003 | INC-2026-003 | 16 Mar 2026 | Relocate cleaning operation to outside sprinkler zone. Review head temperature ratings. | Site Manager | LOW | 30 Apr 2026 |  | Pending | OPEN | False alarm — operational activity | Procedure update in progress. | Pending
📥 Download More Free Industrial Safety Documents at FreeDocumentsHub.com
www.freedocumentshub.com — Available 24 Hours, 7 Days a Week