## Cover Page
FreeDocumentsHub.com
Free Industrial Documents & Training — Available 24/7
GAS DETECTION SYSTEMS FIXED & PORTABLE COMPLETE REFERENCE GUIDE
Hazardous Gas Properties · Detector Types · Alarm Setpoints · Calibration · Inspection Log
| Document Number | FDH-GD-001
| Revision | Rev 00 — Initial Issue
| Document Type | Gas Detection Systems — Fixed & Portable Reference
| Applicable Standard | SAES-B-067 / IEC 60079 / EN 50194 / NFPA 72
| Prepared By | FreeDocumentsHub.com
| Date of Issue | May 2026
© FreeDocumentsHub.com ¦ www.freedocumentshub.com ¦ SAMPLE DOCUMENT

## Gas Types & Hazards
HAZARDOUS GAS TYPES — PROPERTIES, EXPOSURE LIMITS & DETECTION
FDH-GD-001 ¦ Rev 00 ¦ SAES-B-067 / NIOSH / OSHA / Aramco Standards
Gas / Vapour | Chemical Formula | TLV-TWA | STEL | IDLH | Aramco Action Level | Key Properties & Where Found
H2S Hydrogen Sulphide | H₂S | 1 ppm (Aramco action) | 5 ppm | 100 ppm | 1 ppm — all work stops 10 ppm — evacuation | Colourless gas. Rotten egg smell at low conc. — SMELL DISAPPEARS at high conc. (olfactory fatigue). Heavier than air — accumulates in pits, drains, and low points. Found in sour crude, sewer lines, confined spaces, refineries. Most dangerous gas on Aramco projects.
CO Carbon Monoxide | CO | 25 ppm (NIOSH) | 200 ppm | 1,200 ppm | 25 ppm — monitor 200 ppm — evacuate | Colourless, odourless, tasteless — NO warning to senses. Produced by incomplete combustion — generators, vehicles, boilers, fires. Binds to haemoglobin 200× more than oxygen — causes rapid incapacitation and death. Accumulates in enclosed spaces with combustion sources.
LEL Combustible Gas | CH₄/various | N/A — explosion risk not toxicity | N/A | N/A — explosion before IDLH | 10% LEL — stop all Hot Work 25% LEL — evacuate | Lower Explosive Limit (LEL) measures the % of combustible gas concentration at which ignition is possible. Below LEL — too lean to ignite. Above UEL — too rich to ignite. Between LEL and UEL — EXPLOSIVE RANGE. Primary risk on Aramco: methane, LPG, hydrocarbon vapours from process areas.
O2 Deficiency Oxygen | O₂ | 19.5% minimum 23% maximum | N/A | 16% — immediate life threat | Below 19.5% — stop entry / work Above 23% — fire risk | Normal air oxygen: 20.9%. Below 19.5% — not safe for entry (confined space or oxygen-depleted area). Oxygen enrichment above 23% dramatically increases fire and explosion risk — everything burns faster and at lower ignition energy. Can be displaced by CO2, N2, argon, or consumed by oxidation processes inside vessels.
CO2 Carbon Dioxide | CO₂ | 5,000 ppm (0.5%) | 30,000 ppm (3%) | 40,000 ppm (4%) | 5,000 ppm — monitor 30,000 ppm — evacuate | Colourless, odourless gas. Heavier than air — accumulates in low-lying areas. Produced by combustion, fermentation, chemical reactions, and breathing in enclosed spaces. Not acutely toxic at low levels but displaces oxygen. Found in confined spaces, sewers, food storage areas. High concentrations cause rapid unconsciousness.
SO2 Sulphur Dioxide | SO₂ | 0.25 ppm (ACGIH) | 0.5 ppm | 100 ppm | 0.25 ppm — action 1 ppm — evacuate | Colourless gas with sharp, pungent smell. Produced by combustion of sulphur-containing fuels, refinery processes, and volcanic activity. Causes severe respiratory irritation and damage. Found in refineries, power stations, and areas processing sour crude. Heavier than air.
NH3 Ammonia | NH₃ | 25 ppm (NIOSH) | 35 ppm | 300 ppm | 25 ppm — monitor 300 ppm — evacuate | Colourless gas with strong, pungent smell — identifiable at very low concentrations. Lighter than air — rises and accumulates at ceiling level. Found in refrigeration systems, fertiliser production, and water treatment. Highly irritating to respiratory system, eyes, and skin. Flammable at 15–28% concentration in air.
Cl2 Chlorine | Cl₂ | 0.5 ppm (NIOSH) | 1 ppm | 10 ppm | 0.5 ppm — action 1 ppm — evacuate | Greenish-yellow gas with strong, pungent smell. Heavier than air. Produced by chlorination processes, chemical plants, water treatment. Extremely toxic — causes severe respiratory damage. Historical use as chemical weapon demonstrates lethality at low concentrations. Found in petrochemical plants and water treatment facilities.
KEY ABBREVIATIONS
TLV-TWA | Threshold Limit Value — Time Weighted Average. Maximum average concentration for 8-hour shift.
STEL | Short-Term Exposure Limit. Maximum concentration for 15-minute period — maximum 4 times per shift.
IDLH | Immediately Dangerous to Life and Health. Concentration that poses immediate threat to life or causes irreversible health effects.
ppm | Parts Per Million by volume in air. 1 ppm = 0.0001% by volume.
LEL | Lower Explosive Limit. Minimum concentration of gas that can ignite. Below LEL = too lean. Above UEL = too rich. Between = EXPLOSIVE.
UEL | Upper Explosive Limit. Above UEL the mixture is too rich to ignite — but dilution back into the explosive range creates hazard.

## Fixed vs Portable
FIXED GAS DETECTION vs PORTABLE GAS DETECTION — COMPLETE COMPARISON
FDH-GD-001 ¦ Rev 00 ¦ SAES-B-067 / IEC 60079 / EN 50194
Comparison Parameter | FIXED GAS DETECTION SYSTEM | PORTABLE GAS DETECTOR
Detection Principle | Sensors permanently installed at fixed locations throughout the facility. Continuously monitors the atmosphere at those specific points 24 hours a day. Connected to a central Gas Detection Control Panel (GDCP) that processes alarms and activates outputs. | Handheld or body-worn detector carried by the worker. Monitors the atmosphere in the immediate vicinity of the person wearing or holding it. Battery-powered. Requires manual activation, bump testing, and calibration management.
Primary Application | Area monitoring — continuous protection of occupied spaces, process areas, compressor rooms, pump stations, wellheads, utility buildings, and any fixed installation where gas accumulation risk exists. | Personal protection — worker safety during specific tasks: confined space entry, hot work in hydrocarbon areas, maintenance activities, site surveys, and any situation where a worker enters a potentially contaminated atmosphere.
Coverage | Covers the entire defined area continuously — sensors positioned to detect gas accumulation at the most likely points (low points for heavy gases, high points for light gases). Each detector covers a defined detection radius per SAES-B-067. | Covers only the immediate area around the worker — typically a sphere of 1–2 metres radius. Cannot protect unoccupied areas or detect gas accumulation before a worker enters an area.
Response to Alarm | Automatic — alarm activates GDCP, triggers audible and visual alarms at the panel and in the area, can automatically initiate gas shutdown valves, ventilation systems, fire suppression, and ESD systems. No human action required. | Alarm activates buzzer and visual indicators on the detector body — worn by the worker. Requires the worker to take action: stop work, evacuate, notify. No automatic process shutdown capability.
Gas Types Detected | Typically dedicated sensors — one sensor type per target gas (H2S, CO, LEL, O2). Multi-gas fixed systems available but less common. Sensor type specified at design stage based on process hazard study. | Standard 4-gas portable detector measures O2, LEL, CO, and H2S simultaneously. Multi-gas versions available for SO2, NH3, Cl2, and other specific gases. Worker selects detector type based on hazard assessment.
Calibration Requirement | Calibration performed on-site by qualified instrument technician. Frequency: typically every 6 months or per manufacturer's schedule. Requires specialised calibration gas cylinders and equipment. Sensor replacement schedule per manufacturer. | Bump test (function check) required before EVERY use — confirm the detector responds to target gas. Full calibration: per manufacturer's schedule, typically every 6 months. Worker responsibility to bump test. Record kept in detector log.
Response Time | Typically 15–30 seconds from gas reaching the sensor to alarm activation — dependent on sensor technology and gas concentration. Electrochemical sensors fastest for toxic gases. Catalytic bead sensors for LEL. | Response time similar to fixed sensors — 15–30 seconds for the detector itself. BUT: the worker must carry the detector into the gas atmosphere for detection to occur — total response time depends on worker location.
False Alarm Risk | MEDIUM-HIGH — fixed sensors subject to cross-sensitivity from non-target gases, RFI interference, temperature extremes, humidity, and sensor poisoning. Requires careful installation, regular maintenance, and appropriate sensor selection for the environment. | MEDIUM — portable sensors subject to same cross-sensitivity issues. Additional risk from improper storage (silicone exposure), battery issues, and sensor age. Bump test before use is the primary protection against false confidence in a failed sensor.
Cost | HIGH capital cost — sensor heads, cable installation, GDCP panel, commissioning. Ongoing cost: maintenance contracts, calibration gas, sensor replacement. Typical complete fixed system for a process building: USD 15,000–100,000+. | LOWER initial cost — USD 300–2,000 per 4-gas detector. Ongoing cost: calibration gas, sensor replacement, bump test gas. Total cost of ownership over 5 years comparable to fixed systems for high-use applications.
Power Requirement | 24VDC or 230VAC powered from GDCP. Sensor heads typically 2-wire or 3-wire loop-powered at 4–20mA signal output. Battery backup to GDCP required — minimum 24 hours standby per SAES-B-067. | Internal rechargeable battery — typically 8–12 hours per charge. Battery status monitoring built in. Alarm if battery reaches minimum level. USB charging standard on modern detectors.
SAES-B-067 / Aramco Requirement | REQUIRED for all classified hazardous areas on Aramco facilities — process areas, compressor stations, wellheads, pump rooms. Fixed gas detection is NOT optional for classified areas — it is a design requirement. | REQUIRED for all confined space entry, Hot Work in hydrocarbon areas, and any situation where a worker enters a potentially contaminated atmosphere. Cannot substitute for fixed detection in permanently occupied classified areas.
Maintenance | Regular: sensor bump test in-situ, visual inspection, cable and gland inspection, GDCP test. Annual: full sensor calibration, panel function test, output test, battery test. Spare sensors must be kept on site. | Daily: bump test before every use, visual inspection, battery charge check. Six-monthly: full calibration by qualified technician. Annual: sensor replacement if required. Detector log must be maintained.

## Selection Guide
GAS DETECTOR SELECTION GUIDE — BY SPACE AND HAZARD TYPE
FDH-GD-001 ¦ Rev 00 ¦ SAES-B-067 / IEC 60079 / EN 50194
A. SPACE-BASED SELECTION — WHAT TO INSTALL WHERE
Space / Location | Fixed or Portable | Target Gas(es) | Alarm Setpoints | Standard Reference & Notes
Process area — compressor station | Fixed — REQUIRED + Portable for maintenance entry | LEL H2S (if sour service) CO | LEL: 20% / 50% H2S: 1 / 10 ppm CO: 25 / 200 ppm | SAES-B-067 Sec.7. Fixed sensors at low points for heavy gases. One sensor per 50m² minimum. ESD integration required.
Confined space — vessel / tank | Fixed monitoring: N/A Portable 4-gas: MANDATORY before every entry | O2 LEL H2S CO | O2: 19.5% / 23% LEL: 10% H2S: 1 ppm / 10 ppm CO: 25 ppm / 200 ppm | GI-2.100 Confined Space Entry Permit. Atmospheric test before entry AND continuous monitoring during work. Qualified Gas Tester only. Repeat test every hour minimum.
Commercial kitchen — LPG / gas supply | Fixed LEL detector — REQUIRED (Kitchen safety system) Portable for maintenance | LEL (LPG/natural gas) CO (from combustion) | LEL: 25% — alarm LEL: 50% — shutdown + evacuate | SAES-B-067. Sensor positioned at height appropriate for gas type (LPG heavier — low mount, natural gas lighter — high mount). Linked to automatic solenoid valve gas cutoff.
Pump room — hydrocarbon service | Fixed — REQUIRED Portable for maintenance work | LEL H2S (if sour service) | LEL: 20% / 50% H2S: 1 / 10 ppm | SAES-B-067. Sensors at floor level for heavy hydrocarbon vapours. Automatic ventilation activation on first alarm. ESD on second alarm.
Battery room / UPS room | Fixed hydrogen detector — REQUIRED Portable optional for entry | Hydrogen (H2) | H2: 25% LEL (1% vol) — alarm H2: 50% LEL — alarm + vent | Hydrogen lighter than air — sensor mounted at highest point. Automatic ventilation on alarm. No spark-producing equipment inside. IEC 60079 Zone 2 classification.
Generator room | Fixed CO detector — REQUIRED Portable 4-gas for maintenance entry | CO (from exhaust) LEL | CO: 25 ppm / 200 ppm LEL: 20% / 50% | Diesel generator exhaust produces CO. Enclosed generator rooms require CO detection. Exhaust extraction to outside required. Sensor near exhaust and near worker breathing zone.
Hot Work area — field maintenance | Fixed: N/A — temporary area Portable 4-gas: MANDATORY | LEL H2S (if applicable) CO O2 | LEL: 10% — stop Hot Work H2S: 1 ppm CO: 25 ppm O2: 19.5% / 23% | GI-2.100 Hot Work Permit. Gas test before work begins AND if interrupted >30 min. Qualified Gas Tester. Gas reading recorded on permit. Work stops if any alarm triggers.
Wellhead area — oil and gas | Fixed — REQUIRED (multiple) Portable for field workers | H2S LEL CO | H2S: 1 / 10 ppm LEL: 20% / 50% CO: 25 / 200 ppm | SAES-B-067 highest risk area. Multiple sensor points. Wind direction considered for sensor placement. H2S monitors for field workers mandatory. Muster point upwind.
Sewer / drain inspection | Fixed: N/A Portable 4-gas: MANDATORY | H2S O2 LEL CO | O2: 19.5% / 23% LEL: 10% H2S: 1 ppm CO: 25 ppm | Sewer atmosphere can contain all four primary hazards simultaneously. Confined space rules apply. Bump test detector before every entry. Do not enter on zero readings alone — check all 4 gases.
Refrigeration plant — ammonia | Fixed NH3 detector — REQUIRED Portable NH3 for maintenance | Ammonia (NH3) | NH3: 25 ppm — alarm NH3: 300 ppm — evacuate | NH3 lighter than air — sensor at high mount. SCBA required on standby for maintenance. Automatic shutdown of refrigeration compressors on high alarm.
Water treatment — chlorination | Fixed Cl2 detector — REQUIRED Portable Cl2 for entry and maintenance | Chlorine (Cl2) NH3 (if chloramine risk) | Cl2: 0.5 ppm — alarm Cl2: 1 ppm — evacuate | Cl2 heavier than air — sensor at low mount. SCBA mandatory for entry at alarm levels. Immediate evacuation at STEL (1 ppm). Very low IDLH (10 ppm) — margin is small.
Boiler room / fuel gas area | Fixed LEL and CO — REQUIRED Portable for maintenance | LEL (natural gas / LPG) CO | LEL: 20% / 50% CO: 25 / 200 ppm | Natural gas lighter than air — LEL sensor at high mount. CO from incomplete combustion — sensor at breathing zone height. Automatic burner shutdown on LEL high alarm.
Painting / coating area | Fixed LEL — REQUIRED if enclosed Portable LEL for field painting | LEL (solvent vapours) VOCs | LEL: 10% — stop work LEL: 25% — evacuate | Solvent vapours typically heavier than air. Explosion-proof rated equipment required. No ignition sources. Forced ventilation required. Catalytic bead sensor for LEL.
Manhole / underground vault | Fixed: N/A Portable 4-gas: MANDATORY | O2 H2S LEL CO | O2: 19.5% / 23% H2S: 1 ppm LEL: 10% CO: 25 ppm | Confined space. Oxygen displacement by soil gases common. H2S from organic decomposition. Test at top, middle, and bottom of space — stratification possible. Do not lower head in before testing.
Accommodation / camp — LPG kitchen | Fixed LEL — RECOMMENDED CO detector — REQUIRED in sleeping areas | LEL (LPG) CO | LEL: 25% — alarm + cutoff CO: 25 ppm — alarm CO: 70 ppm — evacuate | SAES-B-067 kitchen systems. CO in sleeping areas is life-safety requirement. Fixed CO detectors at breathing zone height. Battery backup mandatory — alarm must function during power failure.
B. FIXED vs PORTABLE QUICK DECISION GUIDE
Situation | Fixed Required? | Portable Required? | Standard | Notes
Permanently occupied classified area | YES — mandatory | YES for maintenance entry | SAES-B-067 | Both required — fixed for continuous protection, portable for workers entering
Confined space entry — any type | NO — fixed not applicable | YES — mandatory by permit | GI-2.100 | Portable 4-gas must be bump tested before every entry
Hot Work in hydrocarbon area | NO — temporary activity | YES — qualified GT required | GI-2.100 | Gas test before work AND every 30 min interruption
Unoccupied process area — inspection | YES if classified area | YES for the inspector | SAES-B-067 | Fixed protects the area — portable protects the person
Emergency response entry | N/A | YES — SCBA AND gas monitor | SAES-B-067 | Never enter an alarm area without gas monitoring and respiratory protection
Kitchen safety system | YES — solenoid valve interlock | For maintenance only | SAES-B-067 | Fixed system mandatory — automatic gas cutoff on alarm

## Inspection & Calibration Log
GAS DETECTOR INSPECTION & CALIBRATION LOG
FDH-GD-001 ¦ Rev 00 ¦ FreeDocumentsHub.com — SAMPLE DOCUMENT
A. FIXED GAS DETECTOR — INSPECTION & CALIBRATION RECORD
Detector Tag No. | Location | Target Gas | Sensor Type | Last Calibration | Next Calibration Due | Bump Test Result | Status / Remarks
GD-001 | Compressor Room — North Wall | H2S | Electrochemical | Jan 2026 | Jul 2026 | PASS — 5 ppm H2S | Operational. Sensor within spec.
GD-002 | Compressor Room — South Wall | LEL | Catalytic Bead | Jan 2026 | Jul 2026 | PASS — 50% LEL | Operational. Bead condition good.
GD-003 | Pump Room — Floor Level | H2S | Electrochemical | Feb 2026 | Aug 2026 | PASS — 5 ppm H2S | Operational.
GD-004 | Pump Room — Ceiling Level | LEL | Catalytic Bead | Feb 2026 | Aug 2026 | PASS — 50% LEL | Operational.
GD-005 | Generator Room — Exhaust Zone | CO | Electrochemical | Mar 2026 | Sep 2026 | PASS — 50 ppm CO | Operational.
GD-006 | Kitchen — Gas Supply Line | LEL | Catalytic Bead | Mar 2026 | Sep 2026 | PASS — 25% LEL | Linked to solenoid valve GV-001.
GD-007 | Battery Room — Ceiling | H2 | Catalytic Bead | Apr 2026 | Oct 2026 | PASS — 25% LEL H2 | Operational. High mount per design.
GD-008 | Wellhead — Area North | H2S | Electrochemical | Apr 2026 | Oct 2026 | PASS — 5 ppm H2S | Wind direction confirmed SW. Sensor OK.
GD-009 | Control Room — Fresh Air Inlet | CO | Electrochemical | May 2026 | Nov 2026 | PASS — 50 ppm CO | Protects fresh air intake.
GD-010 | Chlorination Room — Low Level | Cl2 | Electrochemical | May 2026 | Nov 2026 | PASS — 0.5 ppm Cl2 | SCBA on standby confirmed.
B. PORTABLE GAS DETECTOR — DAILY BUMP TEST & CALIBRATION RECORD
Detector Serial No. | Detector Model | Gases Measured | Last Full Calibration | Next Calibration Due | Today's Date | Bump Test Result | User Name / Signature
PT-001 | Draeger X-am 2500 | O2 / LEL / CO / H2S | Jan 2026 | Jul 2026 | 13 May 2026 | PASS — All 4 gases responded | Naushad / ___
PT-002 | BW GasAlert Max XT II | O2 / LEL / CO / H2S | Jan 2026 | Jul 2026 | 13 May 2026 | PASS — All 4 gases responded | Shahid / ___
PT-003 | Industrial Scientific Ventis MX4 | O2 / LEL / CO / H2S | Feb 2026 | Aug 2026 | 13 May 2026 | PASS — All 4 gases responded | Iftakhar / ___
PT-004 | Honeywell BW Ultra | O2 / LEL / CO / H2S | Feb 2026 | Aug 2026 | 12 May 2026 | PASS — All 4 gases responded | Site Inspector / ___
PT-005 | MSA Altair 4XR | O2 / LEL / CO / H2S | Mar 2026 | Sep 2026 | 11 May 2026 | FAIL — CO sensor no response | REMOVED FROM SERVICE — Sensor replacement required
PT-006 | Draeger X-am 5100 | O2 / H2S specific | Mar 2026 | Sep 2026 | 10 May 2026 | PASS — O2 and H2S responded | Gas Tester / ___
PT-007 | RKI GX-3R | O2 / LEL / CO / H2S | Apr 2026 | Oct 2026 | 13 May 2026 | PASS — All 4 gases responded | Safety Officer / ___
PT-008 | Blackline Safety G7c | O2 / LEL / CO / H2S | Apr 2026 | Oct 2026 | 13 May 2026 | PASS — All 4 gases responded | HSE Supervisor / ___
PT-009 | Crowcon T4 | O2 / LEL / CO / H2S | May 2026 | Nov 2026 | 08 May 2026 | PASS — All 4 gases responded | Maintenance Tech / ___
PT-010 | Honeywell Multirae Lite | O2 / LEL / CO / H2S / VOC | May 2026 | Nov 2026 | 13 May 2026 | PASS — All 5 gases responded | Environmental Monitor / ___
📥 Download More Free Industrial Documents at FreeDocumentsHub.com
www.freedocumentshub.com — Available 24 Hours, 7 Days a Week